## General Site Info
OFF-GRID PUBLIC FACILITIES PV SYSTEM DESIGN TOOL
Version 1.1, December 2022
Developed by the Schatz Energy Research Center at Humboldt State University (www.schatzcenter.org)
This tool is intended to create initial designs of off-grid, stand-alone PV power systems for health care facilities, schools and other public facilities. This tool only considers PV-battery systems, and does not include designs for PV-diesel hybrid systems or grid-connected systems. This tool is intended for project managers and engineers to simplify the design process for such systems during the development of procurement documents. The tool was prepared under the World Bank ROGEAP program and can be used in conjunction with the "Requirements and Guidelines for Installation of Off-grid Solar Systems for Public Facilities with a Focus on Private-Sector-Supprted Service Delivery Models" quality assurance framework (available here: https://www.lightingafrica.org/publication/requirements-and-guidelines-for-installation-of-off-grid-solar-systems-for-public-facilities/) and the "Bid Specification Templates for Off-Grid Solar for Public Facilities".
The tool sizes the PV-battery system for reliability, by designing to ensure the design load is met for a specified number of days of autonomy in the month with the lowest solar radiation. Assumptions regarding efficiency loss throughout the system are included to ensure an adequate system size. Flexibility is built into the tool to allow the user to enter detailed information about specific sites and expected loads, or use default values in the absence of detailed information. Additionally, all assumptions and key inputs can be updated by the user to ensure the tool can be adapted for different circumstances.
Disclaimer: This spreadsheet is intended to be used as an initial tool in estimating the basic parameters of a reliable system. The Schatz Energy Research Center makes no representation, warranty, or guaranty as to the reliability, quality, suitability, availability, accuracy or completeness of the services provided by this tool. By using this tool, users expressly acknowledge that the services are still in the development process, have not been fully tested, and may not operate error-free. Service providers should ensure that systems follow codes of practice for electrical safety and comply with all applicable national and local laws. Specialized codes for electrical installations in medical locations (e.g. IEC 60364-7-710) may also be relevant. This tool is not designed to meet a specific code. Additionally, be aware that this tool offers options to estimate the number of lights and fans needed for a facility based on the dimensions of a building or room. Many facilities are already wired with overhead lights and fans and the automated estimates in this tool may underestimate the total power required for a facility if all the existing (and sometimes inefficient) lights and fans are to be powered by the PV system.
How to use the tool:
In general, inputs should be entered on the six peach-colored tabs, and outputs on the four green tabs, which are formatted as easy-to-print pages. A quick overview of each tab is below and detailed guidance is found on each tab.
General Site Info: The first section of "Required general inputs" should be completed for all sites. The second section "External building dimensions" is optional and only needs to be completed if you want to calculate the recommended numbers of lights and/or fans at the site based on the external dimensions of the site. If you plan to instead manually enter the number of lights and fans for the site, or if you have details of the internal dimensions of each room at the site, then you do not need to complete this section and can move on to the next tab. The third section "Assumptions used to estimate how buildings are proportionally divided into rooms" impact the hours of use assumed for lighting and fans for automated entries in the loads tab. Users only need to interact with this section if they are planning to use the automated entries and want to change the default values.
Detailed Site Info: This tab is optional and should only be completed if you have detailed information about the site including measurements of the available spaces for PV installations (roof tops and pole/ground mounts) and/or measurements of the internal dimensions of each room. The PV information is used to more accurately size the array based on the actual orientation of the modules. The internal dimensions of each room can be used to more accurately estimate the number of lights and fans needed to provide the desired level of service. If you plan to manually enter the number of lights and fans for the site, there is no need to complete the "Building - Internal Dimensions" table.
Solar Resource: The average monthly solar insolation and surface albedo for a site should be entered in this tab. Detailed guidance is provided on this tab regarding sourcing this information from the NASA Power website. Based on the latitude of the site and the tilt and azimuth angles, the daily solar irradiance incident on the PV panels is calculated using the "Tilt Calculations" spreadsheet.
Loads: This tab houses the load profile for the site. You can interact with this tab in several ways. If you want to only include the default set of loads specified for one of 6 different pre-defined system types (Basic Primary Health Clinic, Improved Primary Health Clinic, Basic Comprehensive Health Clinic, Improved Comprehensive Health Clinic, Basic School, or Improved School), you can choose these systems from the dropdown menu at the top of the tab and the loads, quantities, hours of use, electrical characteristics, and load profile will automatically populate. These pre-defined system types are based on the systems described in Section 11.1 of the "Requirements and Guidelines for Installation of Off-Grid Solar Systems for Public Facilities" quality assurance framework. If you instead want to enter your own loads, you can do so by using the dropdown menu to the left of the table and entering any missing values regarding the quantities and hour of use. If you chose not to estimate the numbers of lights and fans using either the external or internal dimensions of the site, you will need to manually specify the numbers and hours of use for lights and fans in the loads table. The automated entries are derived from the "Loads Guide" tab. Values on this tab can be changed if desired, or values that appear in the white cells on the "Loads" tab can be overwritten manually. This tab also includes a number of calculations which are referenced on the Design tab and output tabs.
Design: This tab only has three input values specific to the system design at the top of the sheet, which are followed by the design calculations. To enable the design, you must specify which power draw should be used for inverter sizing and what battery chemistry will be used. Finally, you should adjust the surface azimuth angle (by at a minimum checking due North and due South) to find the optimum angle for the pole-mounted system. This tab references efficiencies, days of autonomy and other key parameters from the "Assumptions" tab - these values can be changed as desired.
Vaccine Fridge: This tab is optional and should only be used if a site has a functional vaccine refrigerator that does not have a working PV system to power it. Vaccine refrigerators should not rely on power from the main PV system and should instead have a dedicated power system. Default assumptions are included on this tab, but if details are known about a PV-battery vaccine refrigerator that is already present at the site but needs a new PV system, or a new PV-battery vaccine refrigerator that is going to be installed, these should be updated. This tab is only meant to calculate PV-battery systems; solar direct drive (battery-less) refrigerators should use manufacturer's calculations for sizing. Note, most new installations of vaccine refrigerators will be solar direct drive based on their increased reliability and longevity.
Output tabs (SiteOverview, SiteSolar, SystemSummary,VaccineSummary): These tabs are intended to provide formatted outputs that can easily be printed as a single PDF document that can be shared as the design for the site. If available, additional information and images should be added to the SiteOverview tab as noted in the guidance notes on that tab. The SiteSolar and SystemSummary tabs need to be reviewed and some rows may need to be hidden or excluded from the print area prior to printing. The VaccineSummary only needs to be output if applicable.
Throughout all of the input tabs, the following color coding is used to indicate the different types of cells:
Text input cells
Numerical input cells
Input cells with dropdown menus
Cells with formulas - locked from editing
Cells with formulas that can be overwritten
Note, dark grey cells are locked from editing to avoid accidental changes. To purposefully edit these cells, unprotect the sheet by going to the "Review" menu and selecting "Unprotect Sheet". No password is required
Many formulas and automated entries rely on the dropdown menus. If the dropdown menus in the blue cells are not functioning, some features may not work - please contact the Schatz Center for assistance.
Required general inputs:
1. Fill in the blue, yellow, and peach cells in this table. Default values have been included to enable the spreadsheet to function, but will be overridden by any user entries.
Site Info
|  |  | User input | Values used in calculations |  | Notes on entries
|  | Type of facility |  | Other |  | Choose health clinic, school or other from dropdown.
|  | Facility Name |  | -- |  | The next 6 fields are not essential for the calculations, but will appear on the output tabs.
|  | Specific type of facility |  | -- |  | These names will vary based on the location, potential options are: PHC, CHC, CSI 1, CSI 2, Primary school, Junior High, Secondary school, etc. This field will appear on the output tabs.
|  | Country |  | --
|  | State |  | --
|  | District |  | --
|  | Open hours per day |  | -- |  | The default load profiles assume that clinics are open 24 hr/day and assume schools offer evening classes. Load profiles can be overwritten on the "Loads" tab if desired.
|  | Latitude |  | -- |  | Enter coordinates in decimal form (XX.XXXXX). Can be approximated using Google Earth or similar if exact location is unknown. The location chosen here should ideally be the same as that used for solar resource data.
|  | Longitude |  | --
|  | Number of buildings |  | 1 |  | Enter the number of buildings intended to be electrified. (Defaults to 1).
|  | Number of staff (Full Time/ Permanent Staff + Support Staff) |  | 5 |  | The number of staff is used to estimate how many mobile phones are likely to be charged each day. (Defaults to 5).
|  | Number of patients per day OR students OR people served |  | -- |  | Not essential for calculations, but will appear on Site Overview output.
|  | Number of staff bedrooms |  | 1 |  | Number of staff bedrooms to be electrified on site. (Defaults to 1).
|  | Number of security posts |  | 1 |  | Number of security posts to be electrified on site. (Defaults to 1).
External building dimensions to estimate numbers of lights and fans (optional):
2. Fill in this table if you want to calculate the recommended numbers of lights and/or fans to include based on the external dimensions of the site. These dimensions could be measured at the site, estimated based on the type of facility, or estimated from Google Earth.
If you already know the number of lights and fans you want to include at a site, this table does not need to be completed and you can fill in information on the "Loads" tab manually. You do not need to fill in the table below and can move on to the next tab.
If you have more detailed information, including room names and room dimensions, more accurate estimates of the numbers of lights and/or fans can be made by entering the internal dimensions on the "Detailed Site Info" tab. You do not need to fill in the table below and can move on to the Detailed Site Info tab.
If you are designing a system where you do not intend to provide lights and fans in every building or every room, only include the dimensions of the areas you intend to equip with lights and fans.
Do you plan to use the external dimensions to estimate lights and fans?
no
Building(s) - External Dimensions
|  | Building |  | Is this a security post? | Length [m] | Width [m] | Area [m2] | Additional Notes
|  | Total area of building(s) |  |  |  | 0
|  | Total area for security post building |  |  |  | 0
|  | Area for staff bedroom(s) |  |  |  | 13.6
|  | Total area excluding security posts and staff bedrooms |  |  |  | -13.6
Assumptions used to estimate how buildings are proportionally divided into rooms (optional):
3. No need to edit below this line unless you want to change general assumptions about how buildings are proportionally divided into rooms. These assumptions impact the hours of use assumed for lighting and fans. If you already know the number and hours of use of lights and fans you want to include at a site, these tables are not relevant and you can fill in information on the "Loads" tab manually. - Rooms with beds and staff bedrooms are assumed to require more hours of fan use than rooms without beds to accommodate use of fans at night. - Security posts are assumed to have one light on 24 hours/day, regardless of the size of the post. These, and all other assumptions about use can be found on the "Loads Guide" and "Assumptions" tabs. Assumptions about the types of rooms and uses are based on facilities in Nigeria. These assumptions would ideally be checked for facilities in other countries.
|  | Building(s) - Internal Dimensions | [6 empty] | Assumptions for health clinics |  | Assumption for staff bedrooms (regardless of size of staff building)
|  | Building | Room Name/ Use |  | % of Building Area | Area [m2] | Additional Notes |  | Room Name/ Use | % of Building Area | Room Name/ Use | Area [m2]
|  | All buildings except security post | Room with bed |  | 0% | 0 |  |  | Consultation room | 16.03% | Staff bedrooms | 13.6
|  | All buildings except security post | Room without bed |  | 100% | -13.6 |  |  | Male ward | 20.04%
|  | Staff quarters | Bedroom |  |  | 13.6 |  |  | Laboratory | 3.643% | Assumption for schools
|  | Security post | Assume single room |  |  | 0 |  |  | Female ward | 10.2% | Room Name/ Use | % of Building Area
[9 empty] | Labor room | 9.69% | Room with bed | 0%
[9 empty] | Toilet | 3.279% | Room without bed | 100%
[9 empty] | Reception | 21.46%
[9 empty] | Hallway | 15.66% | Assumption for other facilities
[9 empty] | Room with bed | 39.93% | Room Name/ Use | % of Building Area
[9 empty] | Room without bed | 60.07% | Room with bed | 0%
[11 empty] | Room without bed | 100%
Congratulations! You are done with general inputs. If you have detailed site information (dimensions of available roof space for PV installations, or interior dimensions of buildings), continue to "Detailed Site Info (Optional)" tab. If you do not have detailed site information, complete remaining entries on the "Loads", "Solar Resource", and "Design" tabs, and, if applicable, the "Vaccine Fridge" tab.
Note on O89: mjh80: Based on the 4 sites in Nigeria with measured staff bedrooms, which were all 13.6 m2

## Detailed Site Info (Optional)
Detailed Site Info: Measurements of available PV spaces and Internal building dimensions
1. Fill in "Available PV Spaces" table below if details of PV sites are available. Follow guidance in the Notes column of the table. Up to 3 PV spaces may be entered. The PV information is used to more accurately size the array based on the actual orientation of the modules and identify if adequate space is available for the full installation. If detailed information about available PV sites is not available, do not make any changes to the tables and the results will assume a pole mount with the ideal angle, tilt, and unlimited space.
2. If you have specific dimensions for all rooms within a facility and want to use these to estimate the number of lights and fans required, fill in the blue and peach columns in the "Internal Dimensions" table. Follow guidance in the column header. If you are designing a system where you do not intend to provide lights and fans in every building or every room, only include the dimensions of the areas you intend to equip with lights and fans.
Note: If you already know the number of lights and fans you want to include at a site, this table does not need to be completed and you can fill in information on the "Loads" tab manually. Similarly, if you indicated on the "General Site Info" tab that you plan to use the external dimensions to estimate lights and fans (by entering "yes" in cell C56) and filling in the External Dimension table, you do not need to fill in the Internal Dimensions table below and can move on to the next tab. In this case, the first four dark gray rows of the "Building - Internal Dimensions" table should present information calculated based on entries in the External Dimensions table. If the "Building - Internal Dimensions" table is completely blank, the tool will not automatically calculate the recommended number of lights and fans and these values will need to be manually entered in the Loads table.
| AVAILABLE PV SPACES |  | Notes | Building - Internal Dimensions
| Identified PV Space #1 name (this space will be considered first) |  | Site name will appear on the SiteSolar output tab. |  | Building | Room Name/ Use | Does this room have a bed? [This must be filled in for lights and fans to automatically calculate.] | Room Number (optional) | Length [m] | Width [m] | Height from floor to ceiling (often 3 m) [m] | Additional Notes | Area [m2] | Volume [m3] | Required Lumens per Room (assuming 162 lm/m2) | Wattage of LED fixtures needed | Rooms in which we will not add fans if they do not already exist (storage, toilet, lab, hallway, entry, kitchen) | Required Fan Count per Room (assuming one 70 W fan/100 m3)
| Array tilt angle [°] |  | Put in the true tilt angle of the roof from the horizontal, the spreadsheet will change it to be at least 10 degrees if needed | These first four rows are automated based on entries for external dimensions on General Site Info tab. If entering internal building dimensions below, these four rows should be blank.
| Length along ridge [m] ((Xridge) |  | Roof example for filling these cells in (if the roof is rectangular, Xridge and Xeave are equal):
Length along eave [m] (Xeave)
Width (at right angle from ridge to eave) [m] (Ywidth)
| PV surface azimuth angle [°] |  | Note: 0° is perfectly south-facing, 90° is perfectly east-facing, -90° is perfectly west-facing, -180° is perfectly north-facing (not +180° in this spreadsheet) | If entering internal building dimensions, start here ->
| Available area of preferred PV site [m2] | 0
| Identified PV Space #2 name (use this space in addition to the above space if the above space is not big enough) |  | See notes for PV Space #1 above
Array tilt angle [°]
Length along ridge [m] ((Xridge)
Length along eave [m] (Xeave)
Width (at right angle from ridge to eave) [m] (Ywidth)
PV surface azimuth angle [°]
| Available area of second PV site [m2] | 0
| Identified PV Space #3 name (use this space in addition to the above space if the above space is not big enough) |  | See notes for PV Space #1 above
Array tilt angle [°]
Length along ridge [m] ((Xridge)
Length along eave [m] (Xeave)
Width (at right angle from ridge to eave) [m] (Ywidth)
PV surface azimuth angle [°]
| Available area of third PV site [m2] | 0
| Is a pole-mounting space or spaces identified? |  | If no area is specified, the spreadsheet will assume there is unlimited space for a pole mount.
Chosen Available area of pole-mounting PV sites [m2]
The protractor and straight lines below can be overlaid on aerial images (from Google Earth or similar) to estimate the available PV sites and angles for the table above, if these were not measured accurately in the field. Paste in the image(s) below and use the protractor to show the angle(s) for future reference.

## Solar Resource
Solar Resource: Monthly insolation, albedo, and shading
1. Follow instructions below this table to find average monthly insolation incident on a horizontal surface as well as surface albedo for the site using the GPS coordinates.
These directions are for accessing NASA's "POWER" database; other databases may be used instead if they offer long-term average monthly insolation and surface albedo on a horizontal surface. [If you want to use generic data for a site with an annual average of 5 kWh/m2/day and minimum monthly of 4.6 kWh/m2/day, you can enter "yes" in cell F9. However, it is better to use site-specific solar data].
2. Paste these average monthly values into rows 26 and 27 and note the data source.
3. If you have site specific shading data for different roof areas, enter the percent not shaded per month from the Solmetric (or similar) data for the site for each site of interest identified.
Generic solar data
| Use generic Solar Data with annual average of 5 kWh/m2/day? |  |  | no | (data is in hidden rows)
This is not recommended. Using data closer to the sites of interest will provide more accurate results.
Generic Solar Data with annual average of 5 kWh/m2/day (from Bubotyo, Uganda near the border of DRC)
GPS coordinates from General Site Info tab:
| Latitude | 0.0977
| Longitude | 29.7922
| Month | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Notes
| Insolation incident on a horizontal surface without shading (kWh/m2/day) | 5.28 | 5.43 | 5.24 | 5.2 | 5.08 | 4.68 | 4.6 | 4.68 | 5.11 | 5.01 | 4.83 | 4.92 | Data from NASA/POWER CERES/MERRA2 Native Resolution Climatology Climatologies retrieved September 2021. 30-year Meteorological and Solar Monthly & Annual Climatologies (January 1990 - December 2019). Elevation from MERRA-2: Average for 0.5 x 0.625 degree lat/lon region = 1333.66 meters ALLSKY_SFC_SW_DWN
| Surface Albedo | 0.16 | 0.16 | 0.16 | 0.16 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | ALLSKY_SRF_ALB
GPS coordinates for solar data:
| Latitude | Missing | These must be filled in and match the solar data being used. Will be automatically populated if using generic solar data, otherwise, enter on the General Site Info tab.
| Longitude | Missing
Solar Resource
| Month | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Notes
Insolation incident on a horizontal surface without shading (kWh/m2/day)
Surface Albedo
| Insolation incident on a horizontal surface without shading (kWh/m2/day) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Surface Albedo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ideal Pole-mount | Tilt [°]: | #N/A | Azimuth [°]: | 0 | [8 empty] | Tilt is the angle from the ground. Azimuth angle of 0° is South facing, -180° is North facing, 90° East facing, -90° West facing
| % not shaded | [12 empty] | 100% not shaded is assumed; if there is shading on the identified space, then enter the % not shaded here (typically between 80 - 99%)
| % not shaded (default 100%) | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
| Insolation incident on the specified tilted surface and surface azimuth angles and considering shading (kWh/m2/day) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | "Tilt Calculations" tab is hidden
| Minimum solar resource (kWh/m2/day) | #N/A
Roof-Mounted PV Sites specified on "Detailed Site Info" tab. [These are optional and do not need to be completed if data is not available]
| PV Site 1 - not identified | Tilt [°]: | #N/A | Azimuth [°]: | 0 | [8 empty] | Tilt is the angle from the ground. Azimuth angle of 0° is South facing, -180° is North facing, 90° East facing, -90° West facing
| % not shaded | [12 empty] | 100% not shaded is assumed; if there is shading on the identified space, then enter the % not shaded here (typically between 80 - 99%)
| % not shaded (default 100%) | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Insolation incident on the specified tilted surface and surface azimuth angles and considering shading (kWh/m2/day) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | "Tilt Calculations" tab is hidden
| Minimum solar resource (kWh/m2/day) | #N/A
| PV Site 2 - not identified | Tilt [°]: | #N/A | Azimuth [°]: | 0
| % not shaded | [12 empty] | 100% not shaded is assumed; if there is shading on the identified space, then enter the % not shaded here (typically between 80 - 99%)
| % not shaded (default 100%) | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Insolation incident on the specified tilted surface and surface azimuth angles and considering shading (kWh/m2/day) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | "Tilt Calculations" tab is hidden
| Minimum solar resource (kWh/m2/day) | #N/A
| PV Site 3 - not identified | Tilt [°]: | #N/A | Azimuth [°]: | 0
| % not shaded | [12 empty] | 100% not shaded is assumed; if there is shading on the identified space, then enter the % not shaded here (typically between 80 - 99%)
| % not shaded (default 100%) | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Insolation incident on the specified tilted surface and surface azimuth angles and considering shading (kWh/m2/day) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | "Tilt Calculations" tab is hidden
| Minimum solar resource (kWh/m2/day) | #N/A
| Go to the POWER Data Access Viewer: |  | https://power.larc.nasa.gov/data-access-viewer/
Here are the steps for accessing the insolation data using this site:
(These directions were last updated September 2021 and are subject to change.)
1. Click "Access Data"; you can also check the box to prevent the "splash screen" from popping up again:
2. In the POWER Single Point Data Access tool, first select "Renewable Energy" and "Climatology" to get long-term averages by month:
3. Enter the latitude and longitude of the site:
There is no need to enter the starting and ending date ranges, because you are accessing climatological data, so you can leave the default values.
Custom climatology is not necessary - you can select "No"
4. Select the CSV file format:
A CSV will make copy-and-pasting values into Excel easiest (CSV = comma-separated values which is a simple text file with minimal formatting; the file can be opened in Excel or similar programs)
5. Scroll down to "select parameters" and expand the category "Solar Fluxes and Related" by clicking the little triangle. (If you click the folder icon instead, you will select everything in the category, so don't do that unless you want to.)
Check the boxes for "All Sky Surface Albedo" and "All Sky Surface Shortwave Downward Irradiance":
Note, the names and categorization of these parameters are subject to change.
If the names have changed, you can look at the "Parameter Definitions" do find the correct parameter. Look for Global horizontal irradiance (GHI) or Insolation incident on a horizontal surface or something similar that implies total irradiance reaching a horizontal surface measured in kWh/m2/day. Do not use parameters for only direct normal or diffuse as these do not provide the total irradiance.
6. Scroll down and click Submit:
8. After a few seconds the results will pop up and the map will show your site. Confirm that GPS coordinates are correct for your intended site. Then click the CSV button:
9. The CSV file should download to your computer for you to open in Excel and copy and paste into the design spreadsheet.
10. Copy and "Paste as values" the ALLSKY_SFC_SW_DWN values into the "Insolation incident on a horizontal surface without shading (kWh/m2/day)" row in the design spreadsheet, and ALLSKY_SRF_ALB into the surface albedo row.
Be aware that the rows may be in the opposite order of how they are saved in this spreadsheet - make sure to match the correct data to the correct row. Additionally note that the final column in the CSV is the annual average (ANN); do not copy this data.

## Loads
Loads: Types, quantities, power, and use
This tab must be completed to determine the total daily energy requirements for the design. Entries on this tab will be grouped by the type of load and presented alphabetically on the "SystemSummary" output tab. You can interact with this tab in several ways:
1. If you want to only include the default set of loads specified for one of 6 different pre-defined system types, you can choose the type of facility and level of service from the dropdown menu in cells D12 and D13. The loads, quantities, hours of use, electrical characteristics, and load profile will automatically populate for these systems. These pre-defined system types are based on the systems described in the "Requirements and Guidelines for Installation of Off-grid Solar Systems for Public Facilities" quality assurance framework. The automated entries are derived from the "Loads Guide" tab. You can change automated entries by either editing the white cells on the "Loads" table or updating the assumptions on the Loads Guide tab. If you want to not include a pre-defined load, you can type "Remove" in the blue cell to the left of the Loads table.
2. If you instead want to enter your own loads, you can do so by selecting a load from the blue dropdown menu to the left of the table and entering any missing values (such as quantities and hours of use) in the white cells for that row.
3. If you want to enter your own loads that are not included in the blue dropdown lists, you can type them in manually in the blue cell (this will trigger a warning, but you can click yes to continue) and fill in information in all of the corresponding white cells (or you can add the new load to the bottom of the "Loads Guide" tab starting in cell F37 and it will appear in the dropdown menu).
4. You can do some combination of the options above by starting with a pre-defined system type and adding/removing loads as desired.
Notes: -If you chose not to estimate the numbers of lights and fans using either the external or internal dimensions of the site (on the General Site Info and Detailed Site Info tabs), you will need to manually specify the numbers and hours of use in the loads table by entering values in the white cells of the Loads table.
-A load profile is presented to enable the designer to visualize the anticipated use of the system during the day and allows for the inverter sizing to either be based on the "Maximum Power Draw over Day Considering Estimated Use Times" or "Maximum Possible Power Draw in a Day". If you want to consider the estimated use times when sizing the inverter, then the load profile must be completed for all loads in the system; otherwise, this section does not necessarily need to be filled in. If using the pre-defined systems, these profiles will automatically populate. If defining your own loads, you will need to enter values in the white cells in columns O to AL. To assist with ensuring the total hours of use in the load profile match the total hours of use per day specified for the load, column N indicates whether hours need to be removed or added to the load profile (warnings in this column can be ignored if the load profile is not being used for sizing, but the "Maximum Power Draw over Day Considering Estimated Use Times " and "Average Power" will be inaccurate).
-The white cells in the Loads table contain formulas, but it is okay to overwrite these with your preferred values. If you want to repopulate a formula that you overwrote, you can copy and paste a cell (not just the formula, but the entire cell) from the same column lower in the table and all references should automatically update.
To automate entries for pre-defined system types, complete the following:
Type of facility:
Level of service:
References for formulas:
Time of use load profile: Estimate the amount of time an appliance is used each hour. Enter a number between 0 -1 in each cell. Cells will automatically populate based on the Loads Guide, but can be overwritten.
[14 empty] | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40
[13 empty] | Total Power if all loads used at same time in that hour (kVA): | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Formulas for making the output look nice on the "System Summary" tab
|  | Loads | [10 empty] | Total Energy per hour (kWh): | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Condensing list of all loads | [10 empty] | Unique loads
|  | Loads (optional user entry - will override any automated entries. If you want to remove an automated load, type "Remove") | Loads (used in calculations) | Quantity | Power per load (W) | Total Power (W) [Power per load x Quantity] | Use per day (h) | Power Factor [0 - 1] | Surge Factor [0 - 1] | Normal VA [Total Power / Power Factor] | Surge VA per equipment | Total hours in load profile [This should match "Use per day". Manually add or remove hours from columns to right to adjust.] | Need to adjust load profile? [Only necessary if using estimated times to determine maximum power draw and average power for inverter sizing] | Used between 00:00 and 01:00 | Used between 01:00 and 02:00 | Used between 02:00 and 03:00 | Used between 03:00 and 04:00 | Used between 04:00 and 05:00 | Used between 05:00 and 06:00 | Used between 06:00 and 07:00 | Used between 07:00 and 08:00 | Used between 08:00 and 09:00 | Used between 09:00 and 10:00 | Used between 10:00 and 11:00 | Used between 11:00 and 12:00 | Used between 12:00 and 13:00 | Used between 13:00 and 14:00 | Used between 14:00 and 15:00 | Used between 15:00 and 16:00 | Used between 16:00 and 17:00 | Used between 17:00 and 18:00 | Used between 18:00 and 19:00 | Used between 19:00 and 20:00 | Used between 20:00 and 21:00 | Used between 21:00 and 22:00 | Used between 22:00 and 23:00 | Used between 23:00 and 24:00 | Maximum Possible Power Draw in a Day [kW] | Maximum Possible Power Draw in a Day (surge not included) [kVA] | Maximum Possible Power Draw in a Day (including worst-case surge) [kVA] | Total Energy Used per Day [kWh] | Maximum Power Draw over Day Considering Estimated Use Times (surge not included) [kVA] | Average Power Draw (kVA) | Total Energy Used over Daytime [kWh] | Total Energy Used over Nighttime [kWh] | -1 | Load | Qty | Power per load (W) | Total Power (W) | Hours of Use | Load | Qty | Power per load (W) | Total Power (W) | Hours of Use |  | Sort Helper | Sorted Unique Loads | Qty | Power per load (W) | Total Power (W) | Average Use (Hours)
[12 empty] | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [28 empty] | Average kVA: | 0 | [14 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [28 empty] | Median kVA: | 0 | [14 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [28 empty] | Min kVA: | 0 | [14 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [28 empty] | Max kVA: | 0 | [14 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
[12 empty] | 0 | [44 empty] | #N/A | 577 | #N/A | 0 | #DIV/0! | 0 | #DIV/0!
Note on O16: Meg: These are to select the appropriate column in the "loads guide" - do not erase or overwrite.
Note on AU18: mjh80: https://www.extendoffice.com/documents/excel/2654-excel-dynamic-list-remove-blanks.html
Note on BF19: mjh80: https://exceljet.net/formula/extract-unique-items-from-a-list
Note on BH19: mjh80: https://trumpexcel.com/sort-data-in-alphabetical-order-formula/

## Design
Design: Main PV + Battery System
To enable the design, you must specify three items:
1. Which power draw should be used for inverter sizing. The "Maximum Possible Power Draw in a Day" option assumes that all loads could be on one time. The "Maximum Power Draw over Day Considering Estimated Use Times" option refers to the load profile specified in the Loads table and looks at the maximum possible draw in any one hour. Using the estimated use times will result in a smaller inverter recommendation, but this could limit the system to not be able to power all loads at once. [Default set at "Maximum Possible Power Draw in a Day"]
2. What battery chemistry will be used (Lead-acid or Lithium-ion). This choice impacts the assumed depth-of-discharge and efficiency of the batteries. These assumptions are listed on the "Assumptions" tab. [Default set at "Lead-acid"]
3. Adjust the surface azimuth angle (by at a minimum checking due North and due South) to find the optimum angle for the pole-mounted system. See detailed guidance in the Design inputs table. [Default set at 0 degrees (due South)]
Once done, review the calculations in the Main PV System Design tab. This tab references efficiencies, days of autonomy and other key parameters from the "Assumptions" tab - these values can be changed as desired.
Design inputs
|  | Which power draw should be used for inverter sizing? |  | Maximum Possible Power Draw in a Day (without surge) [kVA]
|  | Battery chemistry |  | Lead-acid
|  | Surface Azimuth [°] |  | In the cell below, test inputting 0 and -180 to see which azimuth angle creates the smallest PV size in cell D14. Often, sites north of the equator will face due South (0°) and sites south of the equator will face due North (-180°). Some systems above the equator but below the Tropic of Cancer may be best served with an azimuth of due North, which is counterintuitive. This can occur because this design is based on the worst case month; if the month with the least insolation occurs between May and September when the sun is north of the site, an north-facing azimuth may be recommended. (The same is true in reverse for sites south of the equator, but north of the Tropic of Capricorn.) In this spreadsheet, 0° is perfectly south-facing, 90° is perfectly east-facing, -90° is perfectly west-facing, -180° is perfectly north-facing (not +180° in this spreadsheet)
|  |  | (user entry) | 0
|  | Main PV System Design |  | Notes
| PV | Pole-Mounting Option
|  | Surface Azimuth [°] Pole Mount | 0 | Based on user input above. In this spreadsheet, 0° is perfectly south-facing, 90° is perfectly east-facing, -90° is perfectly west-facing, -180° is perfectly north-facing (not +180° in this spreadsheet)
|  | Tilt [°] Pole Mount | #N/A | A tilt of at least 10 degrees is recommended as the minimum tilt angle for PV modules to reduce accumulation of water and dust. The ideal tilt angle is calculated via the "Tilt Calculations" tab. If the ideal tilt is less than 10 degrees, the calculations will still use 10 degrees.
|  | PV power [kW] | #N/A | Total Energy Used per Day * Upgrade Factor * Oversize Factor / Overall System Efficiency / Daily Solar Resource [kWh]*[] *[]/[]/[sun-hours] = [kW]
|  | Estimated site area [m2] needed | #N/A
|  | Available identified pole-mounting space(s) large enough to accommodate sized system? | pole-mounting space yet to be identified | The pole-mount system design will still appear on the output tab, but if the design is larger than the available space, additional space will need to be identified or the loads will need to be reduced.
Roof-Mounted Option
|  | Final PV System Size [kW] | -- | This is the entire PV system size for a roof mounted system (possibly over multiple spaces identified on the "Detailed Site Info" tab). If no areas are identified on the Detailed Site Info tab, then these values will not be calculated. Supporting calculations are below.
|  | Final PV System Area [m2] | --
| Inverter | Average inverter peak power delivered [kVA] | 0 | Maximum Power Draw over Day Considering Estimated Use Times (without surge) [kVA]
|  | Max inverter peak power delivered [kVA] | 0 | Maximum Possible Power Draw in a Day (without surge) [kVA]
|  | Max inverter peak power delivered with surge [kVA] | 0 | Maximum Possible Power Draw in a Day (with surge) [kVA]
| Battery | Battery chemistry | Lead-acid | Designer can choose battery chemistry in inputs table above. If a new battery chemistry is desired, it can be entered and the corresponding efficiency and depth of discharge should be updated on the Assumptions tab. Lead-acid by default
|  | Battery bank capacity [Ah] | 0 | Energy Demand at Battery * Days of Autonomy / System Voltage / DOD [kWh] * 1000 * [] / [V] / [] = [Ah]
|  | Battery bank voltage [V DC] | 12 | Dependent on energy demand [kWh]
|  | Battery large enough to meet potential max discharging current? | yes | Battery should not be discharged at a rate greater than C10 (10 h discharge max). If this cell says "No", the battery bank size should be increased.
Additional System Performance Information
|  | Energy production at battery per day [kWh] | 0 | Total Energy Used per Day * Upgrade Factor * Oversize Factor / System Efficiency related to PV Array [kWh]*[]*[]/[] = [kWh]
|  | Percentage of battery charge per day [%] | #DIV/0! | Total Energy Used per Day / Battery Size [kWh]/([Ah]*[V]) = []
Battery Supporting Calculations
|  | Energy demand at battery by loads downstream of battery [kWh] | 0 | Total Energy Used per Day * Upgrade Factor / System Efficiency not related to PV Array [kWh]*[]/[] = [kwh]
|  | Depth of discharge | 50% | Dependent on battery chemistry
|  | C10 discharge rate [A] | 0 | Battery Bank Capacity / Discharge Period [Ah] / [h] = [A]
|  | Max current to meet peak power demand [A] Should be less than the C10 discharge rate | 0 | Inverter peak power delivered / load voltage [kW] * 1000 / [V] = [A]
PV Roof Mount Supporting Calculations
|  | PV power [kW] needed by space 1 (assuming space 1 can accommodate all needed PV) | -- | Total Energy Used per Day * Upgrade Factor * Oversize Factor / Overall System Efficiency / Daily Solar Resource [kWh]*[] *[]/[]/[sun-hours] = [kW]
|  | Tilt angle of space 1 (°) | -- | Reference Tilt Calculations Spreadsheet
|  | Estimated site area [m2] needed under solar conditions for space 1 | -- | PV Power / Solar Insolation at STC / PV efficiency [kW] / [kW/m2] / [] = m2
|  | Available PV space 1 large enough to accommodate sized system? | -- | --
|  | PV power [kW] provided by space 1 if used to its max | -- | PV Power = site area * Solar Insolation at STC * PV efficiency [kW] = m2 * [] * [kW/m2]
|  | Total daily energy [kWh] provided by space 1 if used to its max | -- | PV power / Upgrade Factor / Oversize Factor * Overall System Efficiency * Daily Solar Resource = Total Energy Used per Day [kWh] = [kW] / [] / [] * [] * [sun-hours]
|  | PV power [kW] needed by space 2 (assuming space 1 is maxed out and more PV is needed) | -- | Total Energy Used per Day * Upgrade Factor * Oversize Factor / Overall System Efficiency / Daily Solar Resource [kWh]*[] *[]/[]/[sun-hours] = [kW]
|  | Tilt angle of space 2 (°) | -- | Reference Tilt Calculations Spreadsheet
|  | Estimated site area [m2] needed under solar conditions for space 2 | -- | PV Power / Solar Insolation at STC / PV efficiency [kW] / [kW/m2] / [] = m2
|  | Available PV space 2 large enough to accommodate remaining needed PV? | -- | --
|  | If PV utilizes and fits in both spaces 1 and 2, then total PV system size [kW] | -- | --
|  | PV power [kW] provided by space 2 if used to its max | -- | PV Power = site area * Solar Insolation at STC * PV efficiency [kW] = m2 * [] * [kW/m2]
|  | Total daily energy [kWh] provided by space 2 if used to its max | -- | PV power / Upgrade Factor / Oversize Factor * Overall System Efficiency * Daily Solar Resource = Total Energy Used per Day [kWh] = [kW] / [] / [] * [] * [sun-hours]
|  | PV power [kW] needed by space 3 (assuming spaces 1 and 2 are maxed out and more PV is needed) | -- | Total Energy Used per Day * Upgrade Factor * Oversize Factor / Overall System Efficiency / Daily Solar Resource [kWh]*[] *[]/[]/[sun-hours] = [kW]
|  | Tilt angle of space 3 (°) | -- | Reference Tilt Calculations Spreadsheet
|  | Estimated site area [m2] needed under solar conditions for space 3 | -- | PV Power / Solar Insolation at STC / PV efficiency [kW] / [kW/m2] / [] = m2
|  | Available PV space 3 large enough to accommodate remaining needed PV? | -- | --
|  | PV power [kW] provided by space 3 if used to its max | -- | PV Power = site area * Solar Insolation at STC * PV efficiency [kW] = m2 * [] * [kW/m2]
|  | Total daily energy [kWh] provided by space 3 if used to its max | -- | PV power / Upgrade Factor / Oversize Factor * Overall System Efficiency * Daily Solar Resource = Total Energy Used per Day [kWh] = [kW] / [] / [] * [] * [sun-hours]
|  | If PV utilizes and fits in all three spaces 1, 2, and 3, then total PV system size [kW] | -- | --

## Vaccine Fridge (Optional)
Vaccine Fridge Design
This tab is optional and should only be used if a site has a functional vaccine refrigerator that does not have a working PV system to power it. Vaccine refrigerators should not rely on power from the main PV system and should instead have a dedicated power system. Default assumptions are included on this tab, but if details are known about a PV-battery vaccine refrigerator that is already present at the site but needs a new PV system, or a new PV-battery vaccine refrigerator that is going to be installed, these should be updated using the peach and blue cells. This tab is only meant to calculate PV-battery systems; solar direct drive (battery-less) refrigerators should use manufacturer's calculations for sizing. Note, most new installations of vaccine refrigerators will be solar direct drive based on their increased reliability and longevity.
Refrigerator Information
|  | Use (h) | 24 | This should always be 24 hours
|  | AC/DC | AC | Choose based on refrigerator
|  | Battery chemistry | Lead-acid | Designer can choose battery chemistry; Lead-acid by default
|  | Voltage | 230 | Typically, 12 or 24 if DC, 120, 220 or 230 if AC
|  | Power (W) | 50 | Calculated as Energy per day/ 24 hours
|  | Energy per Day [kWh] | 1.2 | Default value from 'Loads Guide' tab. Can be overwritten
|  | Power Factor | 0.65 | Default value from 'Loads Guide' tab. Can be overwritten
|  | Surge Factor | 2.2 | Default value from 'Loads Guide' tab. Can be overwritten
|  | Power (VA) | 76.9231
|  | Surge Power (VA) | 169.2308
|  | Vaccine Fridge Design |  | Notes
| PV | Pole-Mounting Option
|  | Surface Azimuth [°] | 0 | 0° is perfectly south-facing, 90° is perfectly east-facing, -90° is perfectly west-facing, -180° is perfectly north-facing (not +180° in this spreadsheet)
|  | Tilt [°] | #N/A | References tilt angle determined for main system
|  | PV power [kW] | #N/A | Total Energy Used per Day * Upgrade Factor * Oversize Factor / Overall System Efficiency / Daily Solar Resource [kWh]*[] *[]/[]/[sun-hours] = [kW]
|  | Estimated site area [m2] needed | #N/A
|  | Available identified pole-mounting space(s) large enough to accommodate vaccine refrigerator system? | pole-mounting space yet to be identified
|  | Available identified pole-mounting space(s) large enough to accommodate main system and vaccine refrigerator system? | pole-mounting space yet to be identified
Roof-Mounted Option
|  | Roof-mounted PV System Size [kW] | -- | This is the entire PV system size for a roof mounted system (possibly over multiple spaces identified on the "Detailed Site Info" tab). Supporting calculations are below.
|  | Roof-mounted PV System Area [m2] | --
| Inverter | Inverter peak power delivered [kVA] | 0.076923 | Maximum Possible Power Draw in a Day (without surge) [kVA]
|  | Inverter peak power delivered with surge [kVA] | 0.16923 | Maximum Possible Power Draw in a Day (with surge) [kVA]
| Battery | Battery chemistry | Lead-acid | Designer can choose battery chemistry in inputs table above Lead-acid by default
|  | Battery bank capacity [Ah] | 926.2964 | Energy Demand at Battery * Days of Autonomy / System Voltage / DOD [kWh] * 1000 * [] / [V] / [] = [Ah]
|  | Battery bank voltage [V DC] | 24 | Dependent on energy demand [kWh]
|  | Battery large enough to meet potential max charging current? | yes | Don't discharge the battery greater than C10 (10 h discharge max)
Additional System Performance Information
|  | Energy production at battery per day [kWh] | 2.0871 | Total Energy Used per Day * Upgrade Factor * Oversize Factor / System Efficiency related to PV Array [kWh]*[]*[]/[] = [kWh]
|  | Percentage of battery charge per day [%] | 9.388% | Total Energy Used per Day / Battery Size [kWh]/([Ah]*[V]) = []
Battery Supporting Calculations
|  | Energy demand at battery by loads downstream of battery [kWh] | 2.2231 | Total Energy Used per Day * Upgrade Factor / System Efficiency not related to PV Array [kWh]*[]/[] = [kwh]
|  | Depth of discharge | 50% | Dependent on battery chemistry
|  | C10 discharge rate [A] | 92.6296 | Battery Bank Capacity / Discharge Period [Ah] / [h] = [A]
|  | Max current to meet peak power demand [A] Should be less than the C10 discharge rate | 0.33445 | Inverter peak power delivered / load voltage [kW] * 1000 / [V] = [A]
|  | PV Roof Mount Supporting Calculations |  | (If you want to calculate roof space required for a separate vaccine fridge, unhide rows 42:62, but note the limitations of the current formulas.)
|  | PV power [kW] needed by space 1 (assuming space 1 can accommodate all needed PV) | #N/A | Total Energy Used per Day * Upgrade Factor * Oversize Factor / Overall System Efficiency / Daily Solar Resource [kWh]*[] *[]/[]/[sun-hours] = [kW] | *This worksheet is set up to work without changes only if the main system design all fits on the first roof space (according to the Detailed Site Info tab) and the additional area needed for the vaccine fridge can also fit on the first roof space. If either of these criteria are not true, then you will need to update these PV Supporting Calculations formulas and make changes to references in the VaccineSummary tab.
|  | Tilt angle of space 1 (°) | #N/A | Reference Tilt Calculations Spreadsheet
|  | Estimated site area [m2] needed under solar conditions for space 1 | #N/A | PV Power / Solar Insolation at STC / PV efficiency [kW] / [kW/m2] / [] = m2
|  | Available PV space 1 large enough to accommodate sized system? | #N/A | --
|  | PV power [kW] provided by space 1 if used to its max | #N/A | PV Power = site area * Solar Insolation at STC * PV efficiency [kW] = m2 * [] * [kW/m2]
|  | Total daily energy [kWh] provided by space 1 if used to its max | #N/A | PV power / Upgrade Factor / Oversize Factor * Overall System Efficiency * Daily Solar Resource = Total Energy Used per Day [kWh] = [kW] / [] / [] * [] * [sun-hours]
|  | PV power [kW] needed by space 2 (assuming space 1 is maxed out and more PV is needed) | #N/A | Total Energy Used per Day * Upgrade Factor * Oversize Factor / Overall System Efficiency / Daily Solar Resource [kWh]*[] *[]/[]/[sun-hours] = [kW]
|  | Tilt angle of space 2 (°) | #N/A | Reference Tilt Calculations Spreadsheet
|  | Estimated site area [m2] needed under solar conditions for space 2 | #N/A | PV Power / Solar Insolation at STC / PV efficiency [kW] / [kW/m2] / [] = m2
|  | Available PV space 2 large enough to accommodate remaining needed PV? | #N/A | --
|  | If PV utilizes and fits in both spaces 1 and 2, then total PV system size [kW] | #N/A | --
|  | PV power [kW] provided by space 2 if used to its max | #N/A | PV Power = site area * Solar Insolation at STC * PV efficiency [kW] = m2 * [] * [kW/m2]
|  | Total daily energy [kWh] provided by space 2 if used to its max | #N/A | PV power / Upgrade Factor / Oversize Factor * Overall System Efficiency * Daily Solar Resource = Total Energy Used per Day [kWh] = [kW] / [] / [] * [] * [sun-hours]
|  | PV power [kW] needed by space 3 (assuming spaces 1 and 2 are maxed out and more PV is needed) | #N/A | Total Energy Used per Day * Upgrade Factor * Oversize Factor / Overall System Efficiency / Daily Solar Resource [kWh]*[] *[]/[]/[sun-hours] = [kW]
|  | Tilt angle of space 3 (°) | #N/A | Reference Tilt Calculations Spreadsheet
|  | Estimated site area [m2] needed under solar conditions for space 3 | #N/A | PV Power / Solar Insolation at STC / PV efficiency [kW] / [kW/m2] / [] = m2
|  | Available PV space 3 large enough to accommodate remaining needed PV? | #N/A | --
|  | PV power [kW] provided by space 3 if used to its max | #N/A | PV Power = site area * Solar Insolation at STC * PV efficiency [kW] = m2 * [] * [kW/m2]
|  | Total daily energy [kWh] provided by space 3 if used to its max | #N/A | PV power / Upgrade Factor / Oversize Factor * Overall System Efficiency * Daily Solar Resource = Total Energy Used per Day [kWh] = [kW] / [] / [] * [] * [sun-hours]
|  | If PV utilizes and fits in all three spaces 1, 2, and 3, then total PV system size [kW] | #N/A | --

## SiteOverview
Site Overview | [9 empty] | Set to print on A4 or Letter paper. Print areas are set, but these can be finicky and may need adjustment.
Country |  | State | District |  |  | Facility Name |  |  | Facility Type | Select all output tabs by ctrl+clicking on the tab label, then print as PDF. Make sure to "ungroup" sheets after printing.
-- |  | -- | -- |  |  | -- |  |  | -- | Rows 5 - 12 should all automatically populate if information on the General Site Info tab is filled in.
| Latitude (°W) | -- |  |  |  |  | Number of buildings | 1
| Longitude (°N) | -- |  |  |  |  | Number of staff | 5
[7 empty] | Number of people served | --
[7 empty] | Open hours per day | --
[7 empty] | Staff housing on site? | Yes
EXISTING SOURCES OF ELECTRICITY
Source |  |  |  | Power (W) | Voltage (V) | Hours available per day | Functional? |  | Notes | Can write in if known from site survey. Add rows if necessary. Do not need to include portable devices.
If your sources have multiple units, remove the units after "Power" in the column heading and write the units in the table (F14)
If the site only has kVA units, change the W to kVA in the "Power" column heading (F14)
This table can be hidden if this information is not known
DESCRIPTION OF EXISTING WIRING and APPLIANCES (if applicable) | [9 empty] | If known from the site survey, write a short description including the condition of the wiring and number of circuits/subpanels. Especially note if wiring will need replacement/upgrading. If there is no existing wiring, write "none".
Example: "There is a 400 A service panel connecting to the main grid and four 200 A subpanels. The wiring in the subpanels is good, but the wiring at the main service panel will need to be upgraded. The facility is equipped with overhead lights and fans, but all are inefficient and should be upgraded."
This can be hidden if this information is not known
NOTES ON SITE | [7 empty] | MAP (google.com/maps) |  | Write in any key observations from the site survey or that you made while designing the site. Can leave blank if there is nothing useful to say.
Add a map of the location of the site, showing where it is within a recognizable space (country, county, etc.).
SITE IMAGE (google.com/earth or from site visit) | [9 empty] | Include a descriptive image of the site that shows the majority of the buildings. This can be google earth if there is a good image or a picture from the site visit.

## SiteSolar
Site Overview
| Country | State | District | Facility Name |  |  |  |  | Facility Type | [8 empty] | The values for the insolation and pole mount should automatically populate from the Solar Resource tab
| -- | -- | -- | -- |  |  |  |  | --
| Month |  |  |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
0 | Insolation incident on a horizontal surface without shading (kWh/m2/day) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Surface Albedo |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ideal Pole-mount |  |  |  | Jan: Tilt [°]:; Mar: #N/A; -- May: Azimuth [°]:; -- Aug: 0
| % not shaded (default 100%) |  |  |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
| Insolation incident on the specified tilted surface and surface azimuth angles and considering shading (kWh/m2/day) |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Minimum solar resource (kWh/m2/day) |  |  |  | Jan: #N/A
| PV Site 1 - not identified |  |  |  | Jan: Tilt [°]:; Mar: #N/A; -- May: Azimuth [°]:; -- Aug: 0 |  | If sites aren't used in designs, HIDE those rows
0 | % not shaded (default 100%) | [15 empty] | 0 | bar: Jan to -- Dec
#N/A | Insolation incident on the specified tilted surface and surface azimuth angles and considering shading (kWh/m2/day) |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
| Minimum solar resource (kWh/m2/day) |  |  |  | Jan: #N/A
| PV Site 2 - not identified |  |  |  | Jan: Tilt [°]:; Mar: #N/A; -- May: Azimuth [°]:; -- Aug: 0
0 | % not shaded (default 100%) | [15 empty] | 0 | bar: Jan to -- Dec
#N/A | Insolation incident on the specified tilted surface and surface azimuth angles and considering shading (kWh/m2/day) |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
| Minimum solar resource (kWh/m2/day) |  |  |  | Jan: #N/A
| PV Site 3 - not identified |  |  |  | Jan: Tilt [°]:; Mar: #N/A; -- May: Azimuth [°]:; -- Aug: 0
0 | % not shaded (default 100%) | [15 empty] | 0 | bar: Jan to -- Dec
#N/A | Insolation incident on the specified tilted surface and surface azimuth angles and considering shading (kWh/m2/day) |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0
| Minimum solar resource (kWh/m2/day) |  |  |  | Jan: #N/A

## SystemSummary
System Design Summary
Design type: |  | Custom
Country |  | State |  | District |  | Facility Name |  |  |  | Facility Type
-- |  | -- |  | -- |  | -- |  |  |  | --
PV |  |  |  | Inverter and Battery |  |  |  |  | Loads and Assumptions |  |  | Values should automatically populate. If roof areas are not identified on the "Detailed Site Info" tab, or the identified areas are too small for the system design, the roof mount design sizing will not appear.
| Ideal Pole Mount: |  |  |  |  | Average power (kVA) | 0 |  |  | Estimated Load (kWh/day) | 0
|  | PV Size (kW) | #N/A |  |  | Max power (kVA) | 0 |  |  | Load growth factor | 1.1
|  | PV array size (m2) | #N/A |  |  | Max power (surge, kVA) | 0 |  |  | Design Load (kWh/day) | 0
|  | Tilt (°) | #N/A |  |  | Max current (A) | 0
[6 empty] | AC Voltage (V) | 230 |  | Existing Loads that are excluded from the system:
| Roof Mount: | [10 empty] | If there are existing loads at the site that should not be connected to the system, (such as air conditioners, autoclave/ sterilizers, resistive heaters, ovens, water heaters), list them here.
|  | PV Size (kW) | -- |  |  | Battery Size (Ah) | 0 |  | -- |  |  | <-If you are doing a design that only provides power for some portions of a facility (like only 3 rooms for a "basic" school system), you can include a note here that says something like: "This design only provides power for 3 rooms and outdoor lighting as shown below. All other existing appliances are excluded."
|  | PV array size (m2) | -- |  |  | Battery Type | Lead-acid
|  | Average Tilt (°) | -- |  |  | Battery Voltage (V) | 12
[6 empty] | Days of Autonomy | 3
|  | System efficiency (%) | 45.06% |  |  | Depth of Discharge (%) | 50%
|  | Module efficiency (%) | 17% |  |  | Max Discharge Rate (h) | 10
|  | PV Oversize factor | 1.2
Load |  |  |  |  | Qty | Power per load (W) | Total Power (W) | Average Use (Hours) |  | Notes |  |  | Columns below are used to make row height size properly if you double-click in the row header despite merged cells.D o not delete or change column widths.
[12 empty] | Add notes manually as needed |  | 0
[12 empty] | Double-click on border between rows in the row header to get row height to automatically size |  | 0
[12 empty] | HIDE unused rows (and the print area should update automatically) |  | 0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0

## VaccineSummary
System Design Summary
Design type: |  | Separate PV + Battery System for Vaccine Refrigerator
Country |  | State |  | District | Facility Name |  |  | Facility Type
-- |  | -- |  | -- | -- |  |  | --
PV |  |  |  | Inverter and Battery |  |  | Loads and Assumptions
| Ideal Pole Mount: |  |  |  | Average power (kVA) | 0.076923 |  | Estimated Load (kWh/day) | 1.2
|  | PV Size (kW) | #N/A |  | Max power (surge, kVA) | 0.16923 |  | Safety Factor | 1.1
|  | PV array size (m2) | #N/A |  | Max current (A) | 0.33445 |  | Design Load (kWh/day) | 1.32
|  | Tilt (°) | #N/A |  | Voltage (V) | 230 AC
Notes:
|  | System efficiency (%) | 45.06% |  | Battery Size (Ah) | 926.2964 | This additional, separate system is solely for powering the facility's PV battery vaccine refrigerator. [Solar direct drive refrigerators should use manufacturer's calculations for sizing.]
|  | Module efficiency (%) | 17% |  | Battery Type | Lead-acid
|  | PV Oversize factor | 1.2 |  | Battery Voltage (V) | 24
[5 empty] | Days of Autonomy | 5
[5 empty] | Depth of Discharge (%) | 50%
[5 empty] | Max Discharge Rate (h) | 10

## Loads Guide
Lighting |  |  | Loads
Light type | Efficacy [lm/W] | If switch to LED, what is the fraction of power while providing the same lumens? | Load Category | Load | Included/ Excluded in General PV System | PHC |  | CHC |  | School |  | Assumption If count is dependent on site info | Basic Hours of Use per Day for Designs | Improved Hours of Use per Day for Designs | Power Draw for Designs (W) | Max current demand (A) | Power factor | Surge factor | Notes | Used between 00:00 and 01:00 | Used between 02:00 and 03:00 | Used between 03:00 and 04:00 | Used between 04:00 and 05:00 | Used between 05:00 and 06:00 | Used between 06:00 and 07:00 | Used between 07:00 and 08:00 | Used between 08:00 and 09:00 | Used between 09:00 and 10:00 | Used between 10:00 and 11:00 | Used between 11:00 and 12:00 | Used between 12:00 and 13:00 | Used between 13:00 and 14:00 | Used between 14:00 and 15:00 | Used between 15:00 and 16:00 | Used between 16:00 and 17:00 | Used between 17:00 and 18:00 | Used between 18:00 and 19:00 | Used between 19:00 and 20:00 | Used between 20:00 and 21:00 | Used between 21:00 and 22:00 | Used between 22:00 and 23:00 | Used between 23:00 and 24:00 | Used between 24:00 and 00:00 | Total hours for appliance over day
[6 empty] | Basic | Improved | Basic | Improved | Basic | Improved | [9 empty] | Used between 02:00 and 03:00 | Used between 03:00 and 04:00 | Used between 04:00 and 05:00 | Used between 05:00 and 06:00 | Used between 06:00 and 07:00 | Used between 07:00 and 08:00 | Used between 08:00 and 09:00 | Used between 09:00 and 10:00 | Used between 10:00 and 11:00 | Used between 11:00 and 12:00 | Used between 12:00 and 13:00 | Used between 13:00 and 14:00 | Used between 14:00 and 15:00 | Used between 15:00 and 16:00 | Used between 16:00 and 17:00 | Used between 17:00 and 18:00 | Used between 18:00 and 19:00 | Used between 19:00 and 20:00 | Used between 20:00 and 21:00 | Used between 21:00 and 22:00 | Used between 22:00 and 23:00 | Used between 23:00 and 24:00 | Used between 24:00 and 00:00
[6 empty] | Number of Units to include in designs | [14 empty] | Used between 02:00 and 03:00 | Used between 03:00 and 04:00 | Used between 04:00 and 05:00 | Used between 05:00 and 06:00 | Used between 06:00 and 07:00 | Used between 07:00 and 08:00 | Used between 08:00 and 09:00 | Used between 09:00 and 10:00 | Used between 10:00 and 11:00 | Used between 11:00 and 12:00 | Used between 12:00 and 13:00 | Used between 13:00 and 14:00 | Used between 14:00 and 15:00 | Used between 15:00 and 16:00 | Used between 16:00 and 17:00 | Used between 17:00 and 18:00 | Used between 18:00 and 19:00 | Used between 19:00 and 20:00 | Used between 20:00 and 21:00 | Used between 21:00 and 22:00 | Used between 22:00 and 23:00 | Used between 23:00 and 24:00 | Used between 24:00 and 00:00 | Total hours for appliance over day | Check Basic | Check Improved
Incandescent | 15 | 0.16667
Fluorescent | 60 | 0.66667 | Communication | Computer (laptop) | Included | 0 | 1 | 1 | 1 | 0 | 1 | -- | 4 | 6 | 60 | 0.27273 | 0.7 | 1 | -- | [8 empty] | 0.75 | 0.75 | 0.75 |  | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | [7 empty] | 6 | 4 | 6
LED | 90 | 1 | Communication | Computer (desktop) | Included | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 6 | 100 | 0.45455 | 0.7 | 1 | Not typically recommended for new systems, but may already be present and/or expected at sites. | [8 empty] | 0.75 | 0.75 | 0.75 |  | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | [7 empty] | 6 | 6 | 6
-- | -- | -- | Communication | USB Modem | Included | 0 | 1 | 1 | 1 | 0 | 1 | -- | 4 | 6 | 2.5 | 0.011364 | 0.7 | 1 | -- | [8 empty] | 0.75 | 0.75 | 0.75 |  | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | [7 empty] | 6 | 4 | 6
https://www.rapidtables.com/calc/light/watt-to-lumen-calculator.html |  |  | Communication | Printer | Included | 0 | 0 | 0 | 0 | 0 | 1 | -- | 1 | 2 | 100 | 0.45455 | 0.7 | 1 | -- | [8 empty] | 0.25 | 0.25 | 0.25 |  | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | [7 empty] | 2 | 1 | 2
|  |  | Communication | Remote Monitoring Platform | Included | 1 | 1 | 1 | 1 | 1 | 1 | -- | 24 | 24 | 5 | 0.022727 | 0.7 | 1 | -- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 24 | 24 | 24
Load requirements based on room area |  |  | Communication | Satellite decoder | Included | 0 | 0 | 0 | 0 | 0 | 0 | -- | 1 | 1 | 35 | 0.15 | 0.9 | 1 | Not typically recommended for new systems, but may already be present and/or expected at sites. | [15 empty] | 0.33333 | 0.33333 | 0.33333 | [6 empty] | 1 | 1 | 1
Lighting (lm/m2) | Fans (# of 70W fans/m3) |  | Communication | DVD player | Included | 0 | 0 | 0 | 0 | 0 | 0 | -- | 1 | 1 | 20 | 0.090909 | 0.9 | 1 | Not typically recommended for new systems, but may already be present and/or expected at sites. | [15 empty] | 1 | [8 empty] | 1 | 1 | 1
162 | 0.01 |  | Communication | Television | Included | 0 | 1 | 0 | 1 | 0 | 1 | 1 TV per staff bedroom | 2 | 4 | 100 | 0.45455 | 0.7 | 1 | -- | [16 empty] | 1 | 1 | 1 | 1 |  |  |  |  | 4 | 2 | 4
|  |  | Communication | Mobile Phones | Included | 5 | 5 | 5 | 5 | 5 | 5 | 1 phone per staff | 1 | 1 | 10 | 0.045455 | 0.7 | 1 | -- | [7 empty] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | [7 empty] | 1 | 1 | 1
Loads typically excluded from PV system, even if they exist at the site |  |  | Lighting | Lighting (general interior) | Included | 0 | 0 | 0 | 0 | 0 | 0 | Based on size of facility (162 lm/m^2). For a "basic" school, only include for 3 rooms | 4 | 6 | 10 | 0.045455 | 0.7 | 1 | The 10 W rating per unit assumes an LED bulb. If tubelights are more commonly used, you can replace this default with 18 W. |  |  |  |  | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  | 6 | 4 | 6
air conditioner, autoclave/ sterilizer, resistive/water heaters, oven | Vaccine refrigerators are typically provided with their own, separate systems, though a designer may want to consider including back-up power for the vaccine refrigerator. |  | Lighting | Lighting (storage/low-use) | Included | 0 | 0 | 0 | 0 | 0 | 0 | Intended to be used for toilets and storage rooms (not labs). Could include more depending on the site. | 1 | 2 | 10 | 0.045455 | 0.7 | 1 | -- |  |  |  |  | 0.5 | [13 empty] | 0.5 | 0.5 | 0.5 |  |  |  | 2 | 1 | 2
|  |  | Lighting | Lighting (outdoor/security) | Included | 4 | 4 | 4 | 4 | 4 | 4 | 4 outdoor lights per building | 10 | 10 | 10 | 0.045455 | 0.7 | 1 | -- | 1 | 1 | 1 | 1 | [14 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 10 | 10 | 10
|  |  | Lighting | Lighting (security post) | Included | 1 | 1 | 1 | 1 | 1 | 1 | 1 light per security post | 24 | 24 | 10 | 0.045455 | 0.7 | 1 | Edit upon judgement Example: security post with 2 rooms for one small site -> treat post as 1 light, or 2 lights with half the time | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 24 | 24
|  |  | Lighting | Lighting (Procedure lamp - LED) | Included | 1 | 1 | 2 | 2 | 0 | 0 | -- | 2 | 4 | 50 | 0.22727 | 0.7 | 1 | -- |  |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 4 | 2 | 4
|  |  | Cooling | Fan (room with bed) | Included | 0 | 0 | 0 | 0 | 0 | 0 | Based on room size: 0 - 100 m^3: 1 fan 101- 200 m^3: 2 fans 201-300 m^3: 3 fans (essentially 1 fan per 100 m^3) Exclude certain rooms - storage, toilet, lab, hallway, entry, kitchen For "basic" school, include for only 3 rooms. | 8 | 12 | 70 | 0.35 | 0.9 | 1.1 | -- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 8 | 12
|  |  | Cooling | Fan (room without bed) | Included | 0 | 0 | 0 | 0 | 0 | 0 |  | 4 | 6 | 70 | 0.35 | 0.9 | 1.1 | -- | [8 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  |  | 6 | 4 | 6
|  |  | Cooling | Fan (lab) | Included | 0 | 0 | 0 | 0 | 0 | 0 | If no existing fan, do not add one, if there is a fan, don't add more | 2 | 6 | 70 | 0.35 | 0.9 | 1.1 | -- | [8 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  |  | 6 | 2 | 6
|  |  | Cooling | Refrigerator/Freezer (General purpose) | Included | 0 | 1 | 1 | 1 | 0 | 0 | -- | 9.36 | 9.36 | 130 | 1.3 | 0.65 | 2.2 | -- | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 9.36 | 9.36 | 9.36
|  |  | MedicalAppliance | Cd4 Machine for HIV | Included | 0 | 0 | 0 | 0 | 0 | 0 | -- | 5 | 5 | 200 | 0.90909 | 0.9 | 1 | Not typically recommended for new systems, but may already be present and/or expected at sites. | [7 empty] | 1 |  | 1 |  | 1 |  | 1 |  | 1 | [8 empty] | 5 | 5 | 5
|  |  | MedicalAppliance | Centrifuge | Included | 0 | 0 | 1 | 1 | 0 | 0 | -- | 2 | 2 | 110 | 0.5 | 0.9 | 1 | -- | [9 empty] | 1 | [6 empty] | 1 | [7 empty] | 2 | 2 | 2
|  |  | MedicalAppliance | Electric Microscope | Included | 0 | 0 | 1 | 1 | 0 | 0 | -- | 2 | 2 | 30 | 0.13636 | 0.7 | 1 | -- | [9 empty] | 1 | [6 empty] | 1 | [7 empty] | 2 | 2 | 2
|  |  | MedicalAppliance | Fetal Heart Monitor | Included | 1 | 1 | 1 | 1 | 0 | 0 | -- | 2 | 2 | 3 | 0.013636 | 0.7 | 1 | -- | [9 empty] | 1 | [6 empty] | 1 | [7 empty] | 2 | 2 | 2
|  |  | MedicalAppliance | Oxygen Concentrator | Included | 0 | 1 | 1 | 1 | 0 | 0 | -- | 4 | 4 | 200 | 0.90909 | 0.9 | 1 | -- |  |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 4 | 4 | 4
|  |  | MedicalAppliance | Portable Ultrasound | Included | 1 | 1 | 1 | 1 | 0 | 0 | -- | 1 | 1 | 28 | 0.12727 | 0.7 | 1 | -- |  |  |  |  | 0.25 |  |  |  |  | 0.25 |  |  |  |  | 0.25 |  |  |  |  | 0.25 |  |  |  |  | 1 | 1 | 1
|  |  | MedicalAppliance | Suction Apparatus | Included | 0 | 0 | 1 | 1 | 0 | 0 | -- | 5 | 5 | 185 | 0.84091 | 0.9 | 1 | -- | [7 empty] | 1 |  |  |  | 1 |  |  |  | 1 |  |  |  | 1 |  |  |  | 1 | 5 | 5 | 5
|  |  | Communication | Palmtop Student Computers | Included | 0 | 0 | 0 | 0 | 0 | 0 | -- | 6 | 6 | 65 | 0.29545 | 0.7 | 1 | -- | [8 empty] | 1 | 1 | 1 | 1 | 1 | 1 | [10 empty] | 6 | 6 | 6
|  |  | Communication | Projector | Included | 0 | 0 | 0 | 0 | 0 | 0 | -- | 6 | 6 | 150 | 0.68182 | 0.7 | 1 | -- | [8 empty] | 1 | 1 | 1 | 1 | 1 | 1 | [10 empty] | 6 | 6 | 6
|  |  | Communication | Laminator | Included | 0 | 0 | 0 | 0 | 0 | 0 | -- | 0.5 | 0.5 | 20 | 0.090909 | 1 | 1 | -- | [9 empty] | 0.5 | [14 empty] | 0.5 | 0.5 | 0.5
|  |  | Medical Appliance | Anesthesia machines | Included | 0 | 0 | 0 | 0 | 0 | 0 | -- | 2 | 2 | 1000 | 4.5455 | 0.9 | 1 | Not typically included, add with caution given high energy requirements | 0.083333 | 0.083333 | 0.083333 | 0.083333 | 0.083333 | 0.083333 | 0.083333 | 0.083333 | 0.083333 | 0.083333 | 0.083333 | 0.083333 | 0.083333 | 0.083333 | 0.083333 | 0.083333 | 0.083333 | 0.083333 | 0.083333 | 0.083333 | 0.083333 | 0.083333 | 0.083333 | 0.083333 | 0.083333 | 2 | 2
|  |  | Medical Appliance | Blood Chemistry Analyzer | Included | 0 | 0 | 0 | 0 | 0 | 0 | -- | 4 | 4 | 88 | 0.4 | 0.9 | 1 | Not typically included, add with caution given high energy requirements | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 4 | 4
|  |  | Medical Appliance | Electrophoresis Genotype Machine | Included | 0 | 0 | 0 | 0 | 0 | 0 |  | 3 | 3 | 190 | 0.86364 | 0.9 | 1 | -- | [8 empty] | 1 | 1 | 1 | [13 empty] | 3 | 3 | 3
|  |  | Medical Appliance | Hematology Analyzer | Included | 0 | 0 | 0 | 0 | 0 | 0 |  | 4 | 4 | 400 | 1.8182 | 0.9 | 1 | -- | [8 empty] | 1 | 1 | 1 | 1 | [12 empty] | 4 | 4 | 4
|  |  | Medical Appliance | Neonatal Incubator | Included | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 24 | 125 | 0.56818 | 1 | 1 | Not typically included, add with caution given high energy requirements | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 24 | 24
|  |  | Medical Appliance | Neonatal Infant Warmer | Included | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 24 | 800 | 3.6364 | 1 | 1 | Not typically included, add with caution given high energy requirements | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 24 | 24
|  |  | Medical Appliance | Patient Monitor for Vital Signs | Included | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 24 | 300 | 1.3636 | 0.9 | 1 | Not typically included, add with caution given high energy requirements | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 24 | 24
|  |  | Medical Appliance | Photoelectric Calorimeter | Included | 0 | 0 | 0 | 0 | 0 | 0 |  | 4 | 4 | 11 | 0.05 | 0.9 | 1 | -- | [8 empty] | 1 | 1 | 1 | 1 | [12 empty] | 4 | 4 | 4
|  |  | Medical Appliance | Phototherapy Device | Included | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 24 | 80 | 0.36364 | 0.7 | 1 | Not typically included, add with caution given high energy requirements | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 24 | 24
|  |  | Medical Appliance | Pulse Oximeter (battery operated) | Included | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 2 | 50 | 0.22727 | 1 | 1 | -- | [13 empty] | 1 | 1 | [9 empty] | 2 | 2 | 2
[44 empty] | 0 | 0 | 0
[44 empty] | 0 | 0 | 0
[44 empty] | 0 | 0 | 0
[44 empty] | 0 | 0 | 0
[44 empty] | 0 | 0 | 0
[44 empty] | 0 | 0 | 0
[44 empty] | 0 | 0 | 0
[44 empty] | 0 | 0 | 0
|  |  |  | Remove | [39 empty] | 0 | 0 | 0
Note on P24: Meg: Assumes 24 hour use with a 39% duty cycle
Note on Q24: Meg: Assumes 24 hour use with a 39% duty cycle

## Assumptions
Assumptions
Value |  | Notes/Source
System Derate Factors |  | Range of Accepted Values from SEI Handbook 2013
Module power tolerance | 0.95 | 0.80-1.05 (PV-related)
Inverter and transformer | 0.72 | 0.88-0.98
Module mismatch | 0.98 | 0.97-0.995 (PV-related)
Temperature losses | 0.88 | page 233 SEI (PV-related)
Diodes and connections | 0.995 | 0.99-0.997 (PV-related)
DC wiring | 0.98 | 0.97-0.99 (PV-related)
AC wiring | 0.99 | 0.98-0.993
Soiling | 0.95 | 0.30-0.995 (PV-related)
System downtime | 0.98 | 0.00-0.995
Battery | 85% | Based on various sources in 2020 (see QA framework for Public Facilities). Energy efficiency ranges are as below, by battery type. Lead-acid: 0.70 - 0.85 Lithium: 0.85 - 0.99 (may be lower if BMS or cooling equipment included)
Vaccine Battery | 85%
Overall system efficiency | 45.06% | From Solar Electric Handbook 2013
Overall system efficiency (AC Vaccine Fridge Only) | 45.06% | Same as "Overall system efficiency" with Vaccine fridge battery type
Overall system efficiency (DC Vaccine Fridge Only) | 63.22% | Same as "Overall system efficiency" minus AC parts and with Vaccine fridge battery type
Efficiency of everything not related to PV | 59.38%
Efficiency of everything not related to PV (AC Vaccine Fridge Only) | 59.38% | Same as "Efficiency of everything not related to PV" with Vaccine fridge battery type
Efficiency of everything not related to PV (DC Vaccine Fridge Only) | 83.3% | Same as "Efficiency of everything not related to PV" minus AC parts and with Vaccine fridge battery type
Efficiency losses related to PV array | 24.11% | From Solar Electric Handbook 2013
Module efficiency | 17% | Estimated based on UNF designs for installations in Uganda 2018
PV array oversize factor | 1.2 | Based on design guidelines from the Pacific Power Association (PPA) and the Sustainable Energy Industry Association of the Pacific Islands (SEIAPI), which recommends oversize factors between 20 - 100%.
Upgrade factor | 1.1 | Increase in system size to account for increase in loads over time, typically 10 - 30%.
Days of autonomy | 3 | Typical recommendations are 3 - 5 days, but could be reduced to 1.5 - 2 if reliability is less important. This value will impact the size and cost of the battery bank and battery replacements.
Days of autonomy (For Vaccine Fridge Only) | 5 | Based on WHO requirement in absence of additional data.
Depth of discharge (DOD) |  | Based on available batteries identified in market scoping in 2018
Lead-acid | 50%
Lithium | 80%
Other
System voltage |  | Based on design guidelines from the Pacific Power Association (PPA) and the Sustainable Energy Industry Association of the Pacific Islands (SEIAPI).
Recommended min energy demand [kWh] | System voltage [V DC]
-- | 12
1 | 24
4 | 48
Max allowable discharge rate (h) | 10 | This is used to check that the maximum power demand does not discharge the battery at too high a rate
Additional Assumptions
Vaccine refrigerators should not be included on the main system, but should have their own, dedicated power system. If the site has an existing vaccine refrigerator that doesn't have its own, functional PV system, a separate PV+battery system can be designed for just the refrigerator on its own using the "Vaccine Fridge" tab. Note, most new vaccine refrigerators are solar direct drive refrigerators that do not require batteries; these should use manufacturer's calculations for sizing and not use this spreadsheet.
Only 1 light is required per security post, no matter how many rooms there are in the security post (this assumes only one light will be on at a time).
Follow these guidelines for rooms having beds or not, unless otherwise specified in the survey or site map. Rooms with beds: -wards, labor room, maternity, bedroom Rooms without beds: -HIV Unit, injection room, office, consultation room, pharmacy, doctor's room, staff room, card room, reception, entry, sitting room, OPD space, store, nutrition room, family planning unit
If specific rooms are entered in the "Detailed Site Info" tab, the calculations will assume the following rooms should not have fans added: labs, toilets, storage rooms (aka store), hallways, entry space, kitchen. The code will exclude rooms with the following in their name: "store","storage","toilet","bath"," lab ", "(lab)", "laboratory"," hall", "hallway", "entry", "kitchen".
All loads are assumed to be 230 VAC.
For the "Basic" school, only provide lights and fans for 3 rooms (this is assuming teachers might want to stay late and they might want to teach an adult education class). You can make this change by reducing the numbers of lights and fans on the Loads tab, or by reducing the square footage of the building entered on the General Site Info tab.
Note on C6: mjh80: Reduced from recommended value of 0.88 due to relatively low capacity factor expected for these systems. The inverter is sized based on the assumption that all loads could be on at one time, but because of the limited hours of use for loads, the average capacity is likely to be very low. A rough analysis for one system suggested the average efficiency for the inverter (weighted based on the amount of power drawn each hour), was approximately 64% - 72%, depending on the distribution of the loads and the assumption of the inverter efficiency.

## List of Items (hidden)
Facility Type | Specific type | Day or Boarding | Building Names | Room Names | Device / Battery Appliances Names | Battery type | If rechargeable, how is it charged? | Electricity-Sources | Fuel-Based | Load Category | Sources of Lighting without Electricity | Lighting | Communication | Heating | Air Cooling | Cooling | Appliances & Devices | Water Supply | Water Pumping Elecricity Source | Misc Loads | Staff housing loads | Payment Entities for Electricity | Payment Entities for Generator/Solar Cost, Maintenance and Repairs | Average Monthly Cost on Electricity Bill | Average Monthly Expenses on Fuel | Average Monthly Expenses on Maintenance/Repair | Sources of Water supply | Where is water supply? | Main use of Water in the Clinic | Duration of water pumping per day | Types of water pumps | Power for water Pumps | Types of Submersible Pumps | If AC, single or 3-phase? | Well material | Water delivery system | Pipe types | Original Condition | Present Condition | Mobile Phones Operators | Internet Providers | Type of Phone | Pump Brand | PV Mounting | Roofing material | Power estimate source | Specific Generation Source Identifiers | Future Power estimate source | Conduit types | Wire type
Health Clinic | Primary Health Care | Day | Classroom | administrative office | Torch/flash light | Alkaline (D-cell, 9V, AA, AAA) | Grid | Grid (National) | Kerosene | Lighting | Kerosene Lantern | Ceiling light | Computers | Biogas Heater | Air conditioner (Cooling unit) | Blood Storage Refrigerator | Anaesthesia machine | Borehole (Electric Pump) | Grid |  | Television | All electricity is metered and billed to patients | Ministry of Health/Primary Health Center head office | None | None | None | Borehole | On-site | Basic Hygiene (Hand washing, Toilet, Bathing) | 30 mins | Submerged | Hand / Manual | Electric Pump (AC Main) | Single | Steel | Carried by hand | White PVC | New | Good | Airtel | Airtel | EDGE | Groundfos SQflex | Roof | Composite shingles | Measured with a kW meter | Mikano Big Size/S20 | Same as existing unit | EMT | Copper
School | Comprehensive Health Care | Boarding | Dormitory | auditorium | Mobile Phone Flash Light | Other non-rechargeable | Solar | Grid (Community) | PMS | Heating | Propane Lantern | Task/security light | Fax | Electric (Unit Heater) | Air conditioner (Space Cooling ) | General purpose Refrigerator | Blood chemistry analyzer | Borehole (Solar Pump) | Generator |  | Radio | Combined funds from donor, facility, ministry (pls detail) | Donors | N500 | N100 | N100 | General Supply from Water Utility | Nearby community | Operating Theatre/ Maternity | 1 hour | Surface | Diesel | Electric Pump (DC Main) | 3-phase | PVC | Piped | Black PVC | Used- good | Fair | Etisalat | Etisalat | HSPA | Lorentz Pump | Ground | Tiles | Measured with a clamp meter and assumed 230 VAC | Newage | Known specifications for identified unit, ex. catalogue, packaging at store | PVC | Aluminum
Police Post | Health Post |  | Exterior | bath / shower room | Solar Lantern | Lithium (mobile phone type) | Hand Crank | Generator (Fuel Operated) | Diesel | Aircooling | Biogas Lantern | Heating Light | Internet Router | Electric (Space Heater) | Evaporative Cooler | Water Dispenser | Bright light microscope | General Supply | Solar |  | Toaster | Donor (pls detail) | Health facility (self) | N550 | N150 | N150 | Hand Pump | Nearby school | Drinking | 1 hour 30 mins | Hand pump | Electric (AC main) |  |  |  | Pump/Storage in facility | CPVC | Used- fair | Bad (needs repair) | GLO | GLO |  |  | Pole | Wood shingles | Measured with a clamp meter and assumed 12 VDC | Sumec Firman | Guess | No conduit, bare wires
E-library | Private Clinic |  | Generator House | children's ward | Tablet | Other rechargeable | Other | Generator (Battery Operated) | Propane | Communication | Battery Rechargeable Lantern | Mobile Phone | Loud Speaker | Gas (Unit Heater) | Fan | Vaccine/Lab Refrigerator | Centrifuge | Hand Pump | Other |  | Laptop | Heath facility (self) | Combination of facility, ministry, and donor sources | N600 | N200 | N200 | Direct Rain |  | Cooking | 2 hours |  | Electric (DC main) |  |  |  |  | Copper | Used- bad | Theft | MTN | MTN |  |  | Mounted to other exisiting structure | Corrugated metal | Measured with a clamp meter and assumed 24 VDC |  | Used rating from other source
Government / Public Building | Primary School |  | Kitchen | classroom | Radio |  |  | Solar (Fixed, standalone) | LNG | Cooling | Battery Torch Light | Torch/flash light | Mobile Phone | Gas (Space Heater) |  | Cow dung | CD4 counter | River |  |  | Desktop | Ministry of Health/Primary Health Care head office | Private purchases by patients or staff | N650 | N250 | N250 | River |  | Cleaning medical equipment | 2 hours 30 mins |  | Solar |  |  |  |  | Steel | Unknown | Scrap (broken and cannot be repaired) | STARCOMMS | IPNX |  |  |  | Other metal roofing | Used rating on appliance's enclosure (or its packaging)
Public Market | Junior Secondary School |  | Laboratory | cold chain | Television |  |  | Solar (Fixed, mini-grid) | Candle | MedicalAppliances | Fire wood | Kerosene Lantern | Radio | Fire wood |  |  | CT scanner | Direct Rain |  |  | Iron | Some electricity is billed to patients (pls detail) | Combination of private purchases and other sources | N700 | N300 | N300 | Stream |  | Laundry | 3 hours |  | Petrol |  |  |  |  | PEX |  | Unknown |  | STARCOMMS |  |  |  | Slate | Used rating from other source
Community water pump | Secondary School |  | Main Building | common room | DVD Player |  |  | Wind (standalone) | Biogas | Waterpumping | Candle | Propane Lantern | Telephone | Cow dung |  |  | ECG | Stream |  |  | Hair dryer | Unknown | Unknown | N750 | N350 | N350 | Purchased in containers/ sachets from outside soruce |  | For Lab Testing | 3 hours 30 mins | [10 empty] | SPECTRANET | [5 empty] | Unicef
Community irrigation system |  |  | Maternity | computer room | Fan |  |  | Wind (mini-grid) | Biomass | Misc | Mobile Phone Flash Light | Biogas Lantern | Television |  |  |  | Electric dry heat sterilizer | Purchased in containers/ sachets from outside soruce |  |  | Mobile Phone Charger | Utility | Utility | N800 | N400 | N400 |  |  |  | 4 hours | [10 empty] | SMILE | [5 empty] | FGN/NPI
|  |  | National Immunization Program (NPI) | consultation room | Medical Device |  |  | Hydropower (small hydropower, standalone) |  |  | Solar Lantern | Electrical Lantern | VHF Radio |  |  |  | Electric equipment sterilization autoclave(pressure and wet heat) |  |  |  | Electric Boling Ring | Facility(self) | Facility(Self) | N850 | N450 | N450 |  |  |  | 4 hours 30 mins | [10 empty] | SWIFT NETWORKS LTD
|  |  | Office | electrical closet |  |  |  | Hydropower (small hydropower, mini-grid) |  |  | Only use main electric lights | Candle | VCR |  |  |  | Electric boiler or steamer (no pressure) |  |  |  | Electric Cooking Stove | N/A | N/A | N900 | N500 | N500 |  |  |  | 5 hours
|  |  | Security Post | entry |  |  |  | Battery (dry cell) |  |  |  |  | Video |  |  |  | ELISA equipment |  |  |  | Rechargeable Lantern |  |  | N950 | N550 | N550 |  |  |  | 5 hours 30 mins
|  |  | Staff Housing | exterior |  |  |  | Battery (rechargable) |  |  |  |  | VCD |  |  |  | Halogen microscope | [6 empty] | N1000 | N600 | N600 |  |  |  | 6 hours
|  |  |  | female ward |  |  |  | Solar (portable + battery rechargable) |  |  |  |  | Projector |  |  |  | Heat source for non-electric equipment | [6 empty] | N1050 | N650 | N650 |  |  |  | 6 hours 30 mins
|  |  |  | generator room |  |  |  | Biogas | [8 empty] | Incubator | [6 empty] | N1100 | N700 | N700 |  |  |  | 7 hours
|  |  |  | gymnasium |  |  |  | UPS | [8 empty] | LED microscope | [6 empty] | N1150 | N750 | N750 |  |  |  | 7 hours 30 mins
|  |  |  | hallway |  |  |  | Whatever electricity is available at the moment | [8 empty] | Mercury or xenon microscope | [6 empty] | N1200 | N800 | N800 |  |  |  | 8 hours
|  |  |  | injection room |  |  |  | Utility+Generator+Solar | [8 empty] | Micro-nebulizer | [6 empty] | N1250 | N850 | N850
|  |  |  | kitchen |  |  |  | Utility+Generator | [8 empty] | Non-electric pot with cover for boiling/steam | [6 empty] | N1300 | N900 | N900
|  |  |  | labor room |  |  |  | Utility+ Solar | [8 empty] | Non-electric equipment sterilization autoclave | [6 empty] | N1350 | N950 | N950
|  |  |  | laboratory |  |  |  | Generator+Solar | [8 empty] | Refrigerator for blood storage | [6 empty] | N1400 | N1000 | N1000
|  |  |  | library |  |  |  | n/a | [8 empty] | Oxygen concentrator | [6 empty] | N1450 | N1050 | N1050
|  |  |  | male ward |  |  |  | unknown | [8 empty] | Solar equipment sterilization autoclave | [6 empty] | N1500 | N1100 | N1100
|  |  |  | maternity | [12 empty] | Suction apparatus | [6 empty] | N1550 | N1150 | N1150
|  |  |  | office | [12 empty] | Ultrasound equipment | [6 empty] | N1600 | N1200 | N1200
|  |  |  | operating theatre | [12 empty] | Vaccine/lab refrigerator | [6 empty] | N1650 | N1250 | N1250
|  |  |  | perimeter of building | [12 empty] | Vacuum aspirator or D&C kit | [6 empty] | N1700 | N1300 | N1300
|  |  |  | perimeter of compound | [12 empty] | Vortex mixer | [6 empty] | N1750 | N1350 | N1350
|  |  |  | personal room / bed room | [12 empty] | Water Purifier | [6 empty] | N1800 | N1400 | N1400
|  |  |  | pharmacy | [12 empty] | Waste autoclave or microwave | [6 empty] | N1850 | N1450 | N1450
|  |  |  | reception | [12 empty] | Waste incinerator | [6 empty] | N1900 | N1500 | N1500
|  |  |  | records | [12 empty] | X-ray machine | [6 empty] | N1950 | N1550 | N1550
|  |  |  | room | [19 empty] | N2000 | N1600 | N1600
|  |  |  | shop | [19 empty] | N2050 | N1650 | N1650
|  |  |  | sitting room | [19 empty] | N2100 | N1700 | N1700
|  |  |  | storage | [19 empty] | N2150 | N1750 | N1750
|  |  |  | surveillance office | [19 empty] | N2200 | N1800 | N1800
|  |  |  | toilet | [19 empty] | N2250 | N1850 | N1850
|  |  |  | waiting room | [19 empty] | N2300 | N1900 | N1900
|  |  |  | Room with bed | [19 empty] | N2350 | N1950 | N1950
|  |  |  | Room without bed | [19 empty] | N2400 | N2000 | N2000
|  |  |  | Bedroom | [19 empty] | N2450 | N2050 | N2050
|  |  |  | Assume single room | [19 empty] | N2500 | N2100 | N2100
[24 empty] | N2550 | N2150 | N2150
[24 empty] | N2600 | N2200 | N2200
[24 empty] | N2650 | N2250 | N2250
[24 empty] | N2700 | N2300 | N2300
[24 empty] | N2750 | N2350 | N2350
[24 empty] | N2800 | N2400 | N2400
[24 empty] | N2850 | N2450 | N2450
[24 empty] | N2900 | N2500 | N2500
[24 empty] | N2950 | N2550 | N2550
[24 empty] | N3000 | N2600 | N2600
[24 empty] | N3050 | N2650 | N2650
[24 empty] | N3100 | N2700 | N2700
[24 empty] | N3150 | N2750 | N2750
[24 empty] | N3200 | N2800 | N2800
[24 empty] | N3250 | N2850 | N2850
[24 empty] | N3300 | N2900 | N2900
[24 empty] | N3350 | N2950 | N2950
[24 empty] | N3400 | N3000 | N3000
[24 empty] | N3450 | N3050 | N3050
[24 empty] | N3500 | N3100 | N3100
[24 empty] | N3550 | N3150 | N3150
[24 empty] | N3600 | N3200 | N3200
[24 empty] | N3650 | N3250 | N3250
[24 empty] | N3700 | N3300 | N3300
[24 empty] | N3750 | N3350 | N3350
[24 empty] | N3800 | N3400 | N3400
[24 empty] | N3850 | N3450 | N3450
[24 empty] | N3900 | N3500 | N3500
[24 empty] | N3950 | N3550 | N3550
[24 empty] | N4000 | N3600 | N3600
[24 empty] | N4050 | N3650 | N3650
[24 empty] | N4100 | N3700 | N3700
[24 empty] | N4150 | N3750 | N3750
[24 empty] | N4200 | N3800 | N3800
[24 empty] | N4250 | N3850 | N3850
[24 empty] | N4300 | N3900 | N3900
[24 empty] | N4350 | N3950 | N3950
[24 empty] | N4400 | N4000 | N4000
[24 empty] | N4450 | N4050 | N4050
[24 empty] | N4500 | N4100 | N4100
[24 empty] | N4550 | N4150 | N4150
[24 empty] | N4600 | N4200 | N4200
[24 empty] | N4650 | N4250 | N4250
[24 empty] | N4700 | N4300 | N4300
[24 empty] | N4750 | N4350 | N4350
[24 empty] | N4800 | N4400 | N4400
[24 empty] | N4850 | N4450 | N4450
[24 empty] | N4900 | N4500 | N4500
[24 empty] | N4950 | N4550 | N4550
[24 empty] | N5000 | N4600 | N4600
[24 empty] | N5050 | N4650 | N4650
[24 empty] | N5100 | N4700 | N4700
[24 empty] | N5150 | N4750 | N4750
[24 empty] | N5200 | N4800 | N4800
[24 empty] | N5250 | N4850 | N4850
[24 empty] | N5300 | N4900 | N4900
[24 empty] | N5350 | N4950 | N4950
[24 empty] | N5400 | N5000 | N5000
[24 empty] | N5450 | N5050 | N5050
[24 empty] | N5500 | N5100 | N5100
[24 empty] | N5550 | N5150 | N5150
[24 empty] | N5600 | N5200 | N5200
[24 empty] | N5650 | N5250 | N5250
[24 empty] | N5700 | N5300 | N5300
[24 empty] | N5750 | N5350 | N5350
[24 empty] | N5800 | N5400 | N5400
[24 empty] | N5850 | N5450 | N5450
[24 empty] | N5900 | N5500 | N5500
[24 empty] | N5950 | N5550 | N5550
[24 empty] | N6000 | N5600 | N5600
[24 empty] | N6050 | N5650 | N5650
[24 empty] | N6100 | N5700 | N5700
[24 empty] | N6150 | N5750 | N5750
[24 empty] | N6200 | N5800 | N5800
[24 empty] | N6250 | N5850 | N5850
[24 empty] | N6300 | N5900 | N5900
[24 empty] | N6350 | N5950 | N5950
[24 empty] | N6400 | N6000 | N6000
[24 empty] | N6450 | N6050 | N6050
[24 empty] | N6500 | N6100 | N6100
[24 empty] | N6550 | N6150 | N6150
[24 empty] | N6600 | N6200 | N6200
[24 empty] | N6650 | N6250 | N6250
[24 empty] | N6700 | N6300 | N6300
[24 empty] | N6750 | N6350 | N6350
[24 empty] | N6800 | N6400 | N6400
[24 empty] | N6850 | N6450 | N6450
[24 empty] | N6900 | N6500 | N6500
[24 empty] | N6950 | N6550 | N6550
[24 empty] | N7000 | N6600 | N6600
[24 empty] | N7050 | N6650 | N6650
[24 empty] | N7100 | N6700 | N6700
[24 empty] | N7150 | N6750 | N6750
[24 empty] | N7200 | N6800 | N6800
[24 empty] | N7250 | N6850 | N6850
[24 empty] | N7300 | N6900 | N6900
[24 empty] | N7350 | N6950 | N6950
[24 empty] | N7400 | N7000 | N7000
[24 empty] | N7450 | N7050 | N7050
[24 empty] | N7500 | N7100 | N7100
[24 empty] | N7550 | N7150 | N7150
[24 empty] | N7600 | N7200 | N7200
[24 empty] | N7650 | N7250 | N7250
[24 empty] | N7700 | N7300 | N7300
[24 empty] | N7750 | N7350 | N7350
[24 empty] | N7800 | N7400 | N7400
[24 empty] | N7850 | N7450 | N7450
[24 empty] | N7900 | N7500 | N7500
[24 empty] | N7950 | N7550 | N7550
[24 empty] | N8000 | N7600 | N7600
[24 empty] | N8050 | N7650 | N7650
[24 empty] | N8100 | N7700 | N7700
[24 empty] | N8150 | N7750 | N7750
[24 empty] | N8200 | N7800 | N7800
[24 empty] | N8250 | N7850 | N7850
[24 empty] | N8300 | N7900 | N7900
[24 empty] | N8350 | N7950 | N7950
[24 empty] | N8400 | N8000 | N8000
[24 empty] | N8450 | N8050 | N8050
[24 empty] | N8500 | N8100 | N8100
[24 empty] | N8550 | N8150 | N8150
[24 empty] | N8600 | N8200 | N8200
[24 empty] | N8650 | N8250 | N8250
[24 empty] | N8700 | N8300 | N8300
[24 empty] | N8750 | N8350 | N8350
[24 empty] | N8800 | N8400 | N8400
[24 empty] | N8850 | N8450 | N8450
[24 empty] | N8900 | N8500 | N8500
[24 empty] | N8950 | N8550 | N8550
[24 empty] | N9000 | N8600 | N8600
[24 empty] | N9050 | N8650 | N8650
[24 empty] | N9100 | N8700 | N8700
[24 empty] | N9150 | N8750 | N8750
[24 empty] | N9200 | N8800 | N8800
[24 empty] | N9250 | N8850 | N8850
[24 empty] | N9300 | N8900 | N8900
[24 empty] | N9350 | N8950 | N8950
[24 empty] | N9400 | N9000 | N9000
[24 empty] | N9450 | N9050 | N9050
[24 empty] | N9500 | N9100 | N9100
[24 empty] | N9550 | N9150 | N9150
[24 empty] | N9600 | N9200 | N9200
[24 empty] | N9650 | N9250 | N9250
[24 empty] | N9700 | N9300 | N9300
[24 empty] | N9750 | N9350 | N9350
[24 empty] | N9800 | N9400 | N9400
[24 empty] | N9850 | N9450 | N9450
[24 empty] | N9900 | N9500 | N9500
[24 empty] | N9950 | N9550 | N9550
[24 empty] | N10000 | N9600 | N9600
[24 empty] | N10050 | N9650 | N9650
[24 empty] | N10100 | N9700 | N9700
[24 empty] | N10150 | N9750 | N9750
[24 empty] | N10200 | N9800 | N9800
[24 empty] | N10250 | N9850 | N9850
[24 empty] | N10300 | N9900 | N9900
[24 empty] | N10350 | N9950 | N9950
[24 empty] | N10400 | N10000 | N10000
[24 empty] | N10450 | N10050 | N10050
[24 empty] | N10500 | N10100 | N10100
[24 empty] | N10550 | N10150 | N10150
[24 empty] | N10600 | N10200 | N10200
[24 empty] | N10650 | N10250 | N10250
[24 empty] | N10700 | N10300 | N10300
[24 empty] | N10750 | N10350 | N10350
[24 empty] | N10800 | N10400 | N10400
[24 empty] | N10850 | N10450 | N10450
[24 empty] | N10900 | N10500 | N10500
[24 empty] | N10950 | N10550 | N10550
[24 empty] | N11000 | N10600 | N10600
[24 empty] | N11050 | N10650 | N10650
[24 empty] | N11100 | N10700 | N10700
[24 empty] | N11150 | N10750 | N10750
[24 empty] | N11200 | N10800 | N10800
[24 empty] | N11250 | N10850 | N10850
[24 empty] | N11300 | N10900 | N10900
[24 empty] | N11350 | N10950 | N10950
[24 empty] | N11400 | N11000 | N11000
[24 empty] | N11450 | N11050 | N11050
[24 empty] | N11500 | N11100 | N11100
[24 empty] | N11550 | N11150 | N11150
[24 empty] | N11600 | N11200 | N11200
[24 empty] | N11650 | N11250 | N11250
[24 empty] | N11700 | N11300 | N11300
[24 empty] | N11750 | N11350 | N11350
[24 empty] | N11800 | N11400 | N11400
[24 empty] | N11850 | N11450 | N11450
[24 empty] | N11900 | N11500 | N11500
[24 empty] | N11950 | N11550 | N11550
[24 empty] | N12000 | N11600 | N11600
[24 empty] | N12050 | N11650 | N11650
[24 empty] | N12100 | N11700 | N11700
[24 empty] | N12150 | N11750 | N11750
[24 empty] | N12200 | N11800 | N11800
[24 empty] | N12250 | N11850 | N11850
[24 empty] | N12300 | N11900 | N11900
[24 empty] | N12350 | N11950 | N11950
[24 empty] | N12400 | N12000 | N12000
[24 empty] | N12450 | N12050 | N12050
[24 empty] | N12500 | N12100 | N12100
[24 empty] | N12550 | N12150 | N12150
[24 empty] | N12600 | N12200 | N12200
[24 empty] | N12650 | N12250 | N12250
[24 empty] | N12700 | N12300 | N12300
[24 empty] | N12750 | N12350 | N12350
[24 empty] | N12800 | N12400 | N12400
[24 empty] | N12850 | N12450 | N12450
[24 empty] | N12900 | N12500 | N12500
[24 empty] | N12950 | N12550 | N12550
[24 empty] | N13000 | N12600 | N12600
[24 empty] | N13050 | N12650 | N12650
[24 empty] | N13100 | N12700 | N12700
[24 empty] | N13150 | N12750 | N12750
[24 empty] | N13200 | N12800 | N12800
[24 empty] | N13250 | N12850 | N12850
[24 empty] | N13300 | N12900 | N12900
[24 empty] | N13350 | N12950 | N12950
[24 empty] | N13400 | N13000 | N13000
[24 empty] | N13450 | N13050 | N13050
[24 empty] | N13500 | N13100 | N13100
[24 empty] | N13550 | N13150 | N13150
[24 empty] | N13600 | N13200 | N13200
[24 empty] | N13650 | N13250 | N13250
[24 empty] | N13700 | N13300 | N13300
[24 empty] | N13750 | N13350 | N13350
[24 empty] | N13800 | N13400 | N13400
[24 empty] | N13850 | N13450 | N13450
[24 empty] | N13900 | N13500 | N13500
[24 empty] | N13950 | N13550 | N13550
[24 empty] | N14000 | N13600 | N13600
[24 empty] | N14050 | N13650 | N13650
[24 empty] | N14100 | N13700 | N13700
[24 empty] | N14150 | N13750 | N13750
[24 empty] | N14200 | N13800 | N13800
[24 empty] | N14250 | N13850 | N13850
[24 empty] | N14300 | N13900 | N13900
[24 empty] | N14350 | N13950 | N13950
[24 empty] | N14400 | N14000 | N14000
[24 empty] | N14450 | N14050 | N14050
[24 empty] | N14500 | N14100 | N14100
[24 empty] | N14550 | N14150 | N14150
[24 empty] | N14600 | N14200 | N14200
[24 empty] | N14650 | N14250 | N14250
[24 empty] | N14700 | N14300 | N14300
[24 empty] | N14750 | N14350 | N14350
[24 empty] | N14800 | N14400 | N14400
[24 empty] | N14850 | N14450 | N14450
[24 empty] | N14900 | N14500 | N14500
[24 empty] | N14950 | N14550 | N14550
[24 empty] | N15000 | N14600 | N14600
[25 empty] | N14650 | N14650
[25 empty] | N14700 | N14700
[25 empty] | N14750 | N14750
[25 empty] | N14800 | N14800
[25 empty] | N14850 | N14850
[25 empty] | N14900 | N14900
[25 empty] | N14950 | N14950
[25 empty] | N15000 | N15000
[25 empty] | N15050 | N15050
[25 empty] | N15100 | N15100
[25 empty] | N15150 | N15150
[25 empty] | N15200 | N15200
[25 empty] | N15250 | N15250
[25 empty] | N15300 | N15300
[25 empty] | N15350 | N15350
[25 empty] | N15400 | N15400
[25 empty] | N15450 | N15450
[25 empty] | N15500 | N15500
[25 empty] | N15550 | N15550
[25 empty] | N15600 | N15600
[25 empty] | N15650 | N15650
[25 empty] | N15700 | N15700
[25 empty] | N15750 | N15750
[25 empty] | N15800 | N15800
[25 empty] | N15850 | N15850
[25 empty] | N15900 | N15900
[25 empty] | N15950 | N15950
[25 empty] | N16000 | N16000
[25 empty] | N16050 | N16050
[25 empty] | N16100 | N16100
[25 empty] | N16150 | N16150
[25 empty] | N16200 | N16200
[25 empty] | N16250 | N16250
[25 empty] | N16300 | N16300
[25 empty] | N16350 | N16350
[25 empty] | N16400 | N16400
[25 empty] | N16450 | N16450
[25 empty] | N16500 | N16500
[25 empty] | N16550 | N16550
[25 empty] | N16600 | N16600
[25 empty] | N16650 | N16650
[25 empty] | N16700 | N16700
[25 empty] | N16750 | N16750
[25 empty] | N16800 | N16800
[25 empty] | N16850 | N16850
[25 empty] | N16900 | N16900
[25 empty] | N16950 | N16950
[25 empty] | N17000 | N17000
[25 empty] | N17050 | N17050
[25 empty] | N17100 | N17100
[25 empty] | N17150 | N17150
[25 empty] | N17200 | N17200
[25 empty] | N17250 | N17250
[25 empty] | N17300 | N17300
[25 empty] | N17350 | N17350
[25 empty] | N17400 | N17400
[25 empty] | N17450 | N17450
[25 empty] | N17500 | N17500
[25 empty] | N17550 | N17550
[25 empty] | N17600 | N17600
[25 empty] | N17650 | N17650
[25 empty] | N17700 | N17700
[25 empty] | N17750 | N17750
[25 empty] | N17800 | N17800
[25 empty] | N17850 | N17850
[25 empty] | N17900 | N17900
[25 empty] | N17950 | N17950
[25 empty] | N18000 | N18000
[25 empty] | N18050 | N18050
[25 empty] | N18100 | N18100
[25 empty] | N18150 | N18150
[25 empty] | N18200 | N18200
[25 empty] | N18250 | N18250
[25 empty] | N18300 | N18300
[25 empty] | N18350 | N18350
[25 empty] | N18400 | N18400
[25 empty] | N18450 | N18450
[25 empty] | N18500 | N18500
[25 empty] | N18550 | N18550
[25 empty] | N18600 | N18600
[25 empty] | N18650 | N18650
[25 empty] | N18700 | N18700
[25 empty] | N18750 | N18750
[25 empty] | N18800 | N18800
[25 empty] | N18850 | N18850
[25 empty] | N18900 | N18900
[25 empty] | N18950 | N18950
[25 empty] | N19000 | N19000
[25 empty] | N19050 | N19050
[25 empty] | N19100 | N19100
[25 empty] | N19150 | N19150
[25 empty] | N19200 | N19200
[25 empty] | N19250 | N19250
[25 empty] | N19300 | N19300
[25 empty] | N19350 | N19350
[25 empty] | N19400 | N19400
[25 empty] | N19450 | N19450
[25 empty] | N19500 | N19500
[25 empty] | N19550 | N19550
[25 empty] | N19600 | N19600
[25 empty] | N19650 | N19650
[25 empty] | N19700 | N19700
[25 empty] | N19750 | N19750
[25 empty] | N19800 | N19800
[25 empty] | N19850 | N19850
[25 empty] | N19900 | N19900
[25 empty] | N19950 | N19950
[25 empty] | N20000 | N20000

## Site Questions & Clarifications
Worksheet | Cell | Unsure About | Issue/Question/Clarification | Suggested Next Steps | Outcome | Status

## Change Log (hidden)
How to save filename: "PVSystemDesignTool-TemplateDateStamp-SiteName-DesignerInitials-ReviewerInitials-date"
Change Batch | Changer | Worksheet | Cell(s) | Change | Status | date
1 | KR | Designs | G6 | Formula - already changed in this spreadsheet | Done
1 | KR | Designs | -- | Add multiple roofs/pole spaces to site info in ranking order of preference Design spreadsheet will go to next preference if first is not big enough Designer can go back and change ranking order if desired after looking at results | Done
1 | KR | Site Info
1 | KR | Intermediate Lighting Interneduate Fan Use Site Info | -- | If a room doesn't have any lighting or fan loads to begin with, then there is an error in the Site Info worksheet. Also, perhaps we should do a special thing for labs since we're not going to add any fans to a lab if none exisit to begin with. | Fixed -actually just needed to extend the number of rooms in the intermediate tab.
1 | KR | Assumptions | B37, B38 | Added two additional assumptions to list. (now 4) | Done
1 | KR | Throughout | -- | read preamble in Recommended Loads guide in RecommendMinEnergy folder: "If a site does not already include in the existing or future loads the recommended number of items listed in columns C-F, add the items to the list of loads for the site. For the "bicycle" systems, only include existing loads + recommended loads. For the "Fiat" systems, include existing + future + recommended loads. If a site lists a future load, but does not specify the desired hours of use and/or power, the values in columns G - J can be used. If large loads, like autoclaves, air conditioners or resistive heaters exist at the site, these should not be included as loads that the system will cover." | 1 - Fixed 2 - Bike already ok; fiat: added spaces in loads guide for future loads we don't already have in the loads guide, made a (F) loads tab altogether and have them included for only fiat loads 3 - I thought we decided to always use the hours and power in our table? 4 - OK
1 | KR | Site Questions & Clarifications | -- | add section in beginning where we can list things we are unsure about | Done
1 | KR | Design | I2 | sensivity analysis for tilt/azimuth | Done
2 | KR | Design | I8 | make the excluded appliances prominent | Done
3 | KR | (E) Loads | -- | make it ok for the site to have no existing loads | This was not a problem to begin with. The problem was that the "(N) Loads (RL & Fans)" tab was incorrectly filled out.
3 | KR | Site Info | C3 | Make a dropdown | Done
3 | KR | Site Info | B8 | say "Number of staff bedrooms" | Done
3 | KR | Site Info | C6 | remove number of patients/students served per day. It's not needed. We used to use it for number of mobile charges before changing the loads guide | Done
3 | KR | Loads tabs and Loads Guide tab | -- | how do we enter a load that doesn't fall into the predetermined categories such as a CD4 machine (for HIV) | Add it to the extended table in the "Loads Guide" tab starting in row 33. Then it will be a dropdown in all the Loads tabs.
4 | KR | Designs and Site Info | -- | How much area is needed for pole mount and if a pole mount site was identified, is it big enough | Done
4 | KR | Loads Guide or Assumptions | -- | Specify which type of room has beds or not | Meg to email Kristen the list - or see row 27
4 | KR | Rec. Loads - Research - Nigeria | -- | Add big loads guide table as reference for future loads we'll accept, like CD4 machines | Added black tab "Rec. Loads - Research - Nigeria"
4 | KR | Loads tabs | -- | Kristen to go through and make sure dropdowns get desktop computer and CD4 machines | Related to row 16 in this tab
4 | KR | (E) Loads tab | B1 | Note somewhere that if an exisiting doesn't have power specified in survey, use loads guide to find it. | Done - Added it to the tab's instructions
4 | KR | (F) Loads tab | B1 | Note somewhere that if an future doesn't have power specified in survey or we are suspect of it, use loads guide to find it. | Done - Added it to the tab's instructions
4 | KR | Site info and (N) Loads (RL & Fans) | -- | Condense RL and Fans into (N) tab from Site info tab | Done
5 | KR | Loads guide | -- | Kwali uses an air conditioner in its lab. Are we sure we want to exclude air conditioners? | MH: I think we should exclude them for now, but make sure it is clear when we go back to talk with the sites that they would be excluded. If the site feels it is a critical load, they can let us know then and we can adjust. 1500 W for 6-10 hours is a lot to add.
5 | KR | Rec. Loads - Research - Nigeria | -- | Not all the information we need is in this reference, e.g. surge and pf | MH: I added what I could, and highlighted the assumptions that we aren't certain of.
5 | KR | Assumptions | 41 | Finish filling out "Follow these guidelines for rooms having beds or not" | Done
6 | MH | Bicycle Loads | -- | Added four columns to be referenced for output - New?, Load, Building, Room, Quantity | Done
6 | MH | Bicycle Loads | B | Load names only appeared if a room name was specified; changed formulas in column B to reference column F on each of the Loads tabs so that loads would appear even if they were not assigned to a specific room or building. | OK
6 | MH | ('E) Loads, (F) Loads, (N) Loads, (N) Loads) | -- | In the formula for the power on each of the Loads tabs, I changed the reference in the Vlookup to 12 instead of 11. It was referencing the hours of use and now references power. | OK
6 | MH | ('E) Loads | AQ | In column AT I changed the formula =IF(AB5="", "",M5*AE5*'Loads Guide'!$C$8) to reference column AE (energy efficiency power) instead of T (existing power). Otherwise, it calculated the lumens needed based on the assumption that the wattage of the LEDs would equal the wattage of existing bulbs, when in the calculations for required power, we used a lower wattage due to the energy efficiency improvements. If this were left to reference the existing power (column T), then we would underestimate the power needed to provide the desired light output. | Check with Kristen to make sure this change is ok KR: Yup, ok
6 | MH | Site Info | U | In column U I changed the formula =IF(Q4="","",MAX(R4,S4)-T4) to use the maximum of either the required light output or the existing light output. When doing energy efficiency upgrades, I don't think we want to reduce the amount of light that people are used to. We can change this back if we want to instead go for just the minimum. | Check with Kristen to make sure this change is ok KR: The way I calculated it, it assumes the existing fixture can be used at the same wattage and the way you did it, it assumes that it can only be used for the same brightness. My will be cheaper to implement since it will require less electrical wiring, e.g. adding less fixtures, and meets our lighting requirement. But maybe it will be easier for the site to have all of the same sized (power) lighting fixtures. -> Decided to go with Meg's suggestion because it makes more sense
6 | MH | Site info | AA | I don't understand the preference for choosing bulbs in column AA. Right now it is set to use a tube light if there are more bulbs than tubes in a room, but otherwise use a bulb. Why? I'm guessing we discussed this, but I can't remember. Also, I'm wondering if it is supposed to be referencing columns Z and Y instead. | Kristen fixed. Meg confirmed that we want to go with bulbs if the tube and bulb count are equal.
6 | MH | Site info | AI | Added a column to check for rooms that we do not want to add fans in. Then changed formula in column AI to =IF(P4="","",IF(AH4="No new fan",0,P4*'Loads Guide'!$C$14)) to exclude adding new fans in those rooms. | OK
6 | MH | Site info | B:C | Added 4 rows to site info for Country, State, District and Facility name | Done
6 | MH | Bicycle Loads | AT: | Added columns to condense list of loads | Done
6 | MH | BicycleLoadsOut |  | Made new sheets that outputs site overview, design summary and detailed loads | Done
6 | MH | Loads Guide | G | Shortened a few of the load names for output. Changed: Remote Monitoring Platform, Lighting (storage/low-use), Lighting (Angle poise lamp), Electric Microscope, Fetal Heart Monitor. This will impact us when copying data into the new spreadsheet; the main one that might need updating is "Lighting (storage/low-use)". | Done
6 | MH | ('E) Loads | AA | Specific to Kwali, not template: Updated entries in AA where toilets and storage were not marked as "Lighting (storage/low-use)" | Done
6 | MH | Site info |  | Added field for # of patients/students (needed for output, not calculations). Rearranged initial entries to better align with survey form | Done
6 | MH | Designs | Row 12 | Added parenthesis and factor of 1000 to equation for % of battery bank charged each day. | Done
6 | MH | ('E) Loads | AR | Added to if statement so that if the power was not included in the survey (which was common in Niger), the power will be referenced from the Loads Guide | Done
6 | MH | (F) Loads | AK | Added to if statement so that if the power was not included in the survey (which was common in Niger), the power will be referenced from the Loads Guide | Done
6 | MH | Designs | Rows 7, 11, 12 and 33 | I have questions about the calculations as noted in the comments | Kristen reviewed calcs - no issues found that effect design. Kristen responded to all Megs comments.
7 | ST | BicycleSummary, FiatSummary | Rows 11, 16 | Changed kWp to kW | Done
7 | ST | Fiat Loads | H437-H580 | Changed formula to [IF(G437="Included",'(N) Loads (Sans RL&F)'!P4,"")] to reference the column P instead of O | Done
7 | ST | Fiat Loads | AT: | Copied MH updates (dded columns to condense list of loads) | Done
7 | ST | FiatLoadsOut |  | Copied MH updates (Made new sheets that outputs site overview, design summary and detailed loads) | Done
7 | ST | Fiat Loads | H437-H580 | Changed formula to [IF(G437="Included",'(N) Loads (Sans RL&F)'!P4,"")] to reference the column P instead of O | Done
7 | ST | Site Solar |  | reformatted tab | Done
8 | KR | (E) Loads (F) Loads | Column AP | Meg suggested that we call on the loads entry instead of the room entry in case people don't fill out the spreadsheet completely. | Done
8 | KR | Assumptions (F) Loads | Row 42 | Fans are not added to labs, toilets, storage rooms, or ? | Done
8 | KR | (E) Loads | Column AU | Changed =IF(AA5="","",IF(OR(AP5="needed",NOT(ISNUMBER(W5))),M5*VLOOKUP(AA5,'Loads Guide'!$G$6:$R$60,12,0),IF(AE5<>"",M5*AE5,IF(H5="Yes","make an estimate to account for energy efficiency",W5)))) to =IF(AA5="","",IF(AE5<>"",M5*AE5,IF(H5="Yes","make an estimate to account for energy efficiency",IF(NOT(ISNUMBER(T5)),M5*VLOOKUP(AA5,'Loads Guide'!$G$6:$R$60,12,0),W5)))) * Removed AP5="needed" because none of them will be "needed" in this sheet anymore * Since someone added in a check that a power value was correctly recorded, things got out of order. For example, if the surveyor didn't record a power value for a tube light, then the current formula assumes a bulb light (only the power for a bulb light is in the loads guide). | MH: Thanks for catching this - though I think this is still an issue where if they do not enter a power, the power of a bulb light will be used for a tube light. Should we change it to: =IF(AA5="","",IF(AE5<>"",M5*AE5,IF(H5="Yes","make an estimate to account for energy efficiency",IF(AND(NOT(ISNUMBER(T5)),AC5="tube"),M5*'Site Info'!$F$4,IF(AND(NOT(ISNUMBER(T5)),M5*VLOOKUP(AA5,'Loads Guide'!$G$6:$R$60,12,0),W5)))) KR: You should try it out the way it is. For example, delete the contents of cell T8 in (E ) Loads, you see that AU8 gives 18. Then change column 8's bulb type from tube to bulb and you get 10. Meg says ok to this.
8 | KR | (F) Loads | Column AK | Changed =IF(W6="","",IF(NOT(ISNUMBER(P6)),J6*VLOOKUP(AA6,'Loads Guide'!$G$6:$R$60,12,0),S6)) to =IF(W6="","",IF(AA6<>"",J6*AA6,IF(NOT(ISNUMBER(P6)),J6*VLOOKUP(W6,'Loads Guide'!$G$6:$R$60,12,0),S6))) * It didn't consider energy efficiency | Done
8 | KR | (N) Loads (Room Lights & Fans) (N) Loads (Sans RL&F) | Row 2 | Changed the title of "New" to "Needed" | Done
8 | KR | Loads Guide (E ) Loads (F) Loads (N) Loads (Room Lights & Fans) (N) Loads (Sans RL&F) | Profile sections | Do we care about estimating when loads will be used, e.g. how this could effect inverter efficiency? | Yes- let's add. Meg will create a profile and then compare to Kristen and Scott's. Then Kristen will update the code in the spreadsheet. KR: Spreadsheet updated to take in Meg's profile when ready.
9 | MH | Site Info | Column AA | Changed decision for bulbs vs. tubes to be based on the amount of additional wattage each choice would provide. Optimized for lowest additional wattage: =IF(V25="","",IF(V25="--","--",IF(($Y25*$F$4)<($Z25*$F$5),$E$4,$E$5))) | Done
10 | KR/MH | Site Info | M3 | Changed column title to Height from floor to ceiling [m] | Done - transcribed from Kristen's changes on the template
10 | KR/MH | Site Info | Row 8 | Added colum to ask: If school, specify school type | Done - transcribed from Kristen's changes on the template
10 | KR/MH | Site Info | Row 7 | Made the dropdown only PCH, CHC, and School, otherwise code later on gets messed up for school types | Done - transcribed from Kristen's changes on the template
10 | KR/MH | Site Info | E8 | Added a table to keep record of who is filling out this spreadsheet per site | Done - transcribed from Kristen's changes on the template
11 | MH | Bicycle Loads | Columns C, I | Added column C to allow designer to exclude specific loads or rooms (this way the school Bicycle and Fiat can be done on the same spreadsheet). Changed the formulas in column H to write "Excluded" if the designer marked a given load as "Exclude". | Done | 2018-09-10
11 | MH | Fiat Loads | Columns C, I | Added column C to allow designer to exclude specific loads or rooms (this way the school Bicycle and Fiat can be done on the same spreadsheet). Changed the formulas in column H to write "Excluded" if the designer marked a given load as "Exclude". | Done | 2018-09-10
11 | MH | Site Info | Column AG | Fixed formula so it referenced the bulb column if LED bulbs was specified. =IF(AA4=$E$4,IF(AE4="--",0,AE4),IF(AA4=$E$5,IF(AF4="--",0,AF4),IF(AA4="--","--",""))) | Done | 2018-09-10
11 | MH | (N) Loads (Room Lights & Fans) | Columns L, M and P | Changed Vlookups for fans to reference columns 21, 23 and 15, respectively (previously referenced 20, 22 and 15; probably a column was added at some point). | Done | 2018-09-10
11 | MH | (N) Loads (Sans RL&F) | Column S | Changed Vlookup for surge current to reference column 15 (was referencing 14) | Done | 2018-09-10
11 | MH | Bicycle Loads and Fiat Loads | Column F | Added a column to state whether the light points are bulbs or tubes | Done | 2018-09-10
11 | MH | Bicycle Loads and Fiat Loads | Column AW | Changed formula to alter the names of lights and fans to simplify outputs. =IF($AV4="","",IF(E4="","",IF(F4<>"",CONCATENATE("Lighting - ",F4),IF(E4="Fan (bed-less room)","Fan",IF(E4="Fan (room with bed)","Fan",IF(E4="Fan (lab)","Fan",E4)))))) | Done | 2018-09-10
11 | MH | Bicycle Loads and Fiat Loads | Columns BN-BQ | Changed formulas to reference new load names | Done | 2018-09-10
11 | MH | Bicycle and Fiat Summary | Column U | Added a column to make it possible for the rows to automatically resize properly. Changed spacer rows to a font size of 4. Now before printing, select the spreadsheet and doubleclick on a row line to make sure all text is shown. Decided not to add kWh becuase the total does not match the energy used in the table above due to differences in the power and hours within a given category. | Done | 2018-09-10
11 | MH | Bicycle and Fiat Loads Out | Column R | Added a column to make it possible for the rows to automatically resize properly. Changed spacer rows to a font size of 4. Now before printing, select the spreadsheet and doubleclick on a row line to make sure all text is shown. | Done | 2018-09-10
11 | MH | Bicycle and Fiat Loads (Kwali) | Column C | Kwali Specific: Bicycle Loads and Fiat Loads. Marked laptop as "Exclude" since the system already has a desktop | done | 2018-09-10
11 | MH | (N) Loads (Room Lights & Fans)(Kwali) | F30 | Kwali Specific: Changed load type of Maternity Office fan from "Fan (lab)" to "Fan (bed-less room)" | done | 2018-09-10
11 | MH | Output spreadsheets |  | Updated "Facility Type" to reference new "specify school type" cell C8 on Site Info tab | Done | 2018-09-10
11 | MH | Assumptions |  | Added an assumption about electrifying only 3 rooms for schools. | Done | 2018-09-10
11 | MH | Loads Guide |  | Updated a few loads guide assumptions to match our recommended loads spreadsheet, such as removing the refrigerators for schools. | Done | 2018-09-10
12 | KVW | Site Info | AM4:AM58 | Changed end of IF statement in equation to report "0" instead of "--" because dependent cell's equations were having trouble calculating "--" or even "" | done- and updated in Kwali-mh2 | 2018-09-11
12 | KVW | (N) Loads (Room Lights & Fans) | P4:P1000 | updated referencing cell from 14 to 15 in Vlookup because col was reporting the power factor from col 14 instead of surge factor in col 15 | done (I had previously made this change in Kwali, it is strange that it reverted. Should we be worried that other changes reverted too? -mh) OK-KVW | 2018-09-11
12 | KVW | SiteOverview | N15:16 | Added comments for guidance for inputting power ratings units (W, kVA) and to update the column header in cell F14 when appropriate | done- and updated in Kwali-mh2 | 2018-09-11
12 | KVW | Summary green tabs |  | updated all the site name cells to autopopulate from Site Info along with the other header site information | done-and updated in Kwali-mh2 | 2018-09-11
13 | MH | (N) Loads (Room Lights & Fans) | Column N | For some reason, the VLOOKUP for fans in column N was still referencing the 20th cell, changed this to 21. (I caught this because the output had no fans in the basic system) | done (I had previously made this change in Kwali, it is strange that it reverted. Should we be worried that other changes reverted too? -mh OK-Kvw | 2018-09-11
13 | MH | Fiat Loads | J327:J426 | Changed quantity reference to column M to reference the Fiat quantity instead of the bicycle quantity. (I caught this because there was 1 more fan in the Fiat system than in the Basic system, but both should have had 8 fans.) | done-and updated in Kwali-mh2 | 2018-09-11
13 | MH | Bicycle Loads and Fiat Loads | Columns G and H | Changed the check for "unassigned" to look in columns B and C of the respective tabs. I noticed on the load output tabs that cases where the building was assigned, but the room wasn't assigned were left blank. | done-and update in Kwali-mh2 | 2018-09-11
13 | MH | Site info | columns AB, AG and AK | Updated to output 0 if a site has no additional lights and/or fans to fix potential "#N/A" problem that Kaileigh experienced with the Fiat fans. | done-and updated in Kwali-mh2 | 2018-09-11
13 | MH | Site info | Column AN | Because the condensing list equations were based on the "--" output of columns AB and AK, also updated these to also exclude sites with "0". (Note this formula changes from referencing column AB in rows 4:59 to referncing column AK thereafter). | done-and updated in Kwali-mh2 | 2018-09-11
14 | KR | (E) Loads | Column W | Looks like someone changed the formula but didn't drag it down to the end of the table. I draffed it down to the end of the table. | done -and updated in Kwali KR | 2018-09-12
14 | KR | Site Questions & Clarifications | Row 12 | Added the file name instructions back to the top of this tab. I disappeared between versions. | Done just for blank. | 2018-09-12
14 | KR | Site Info | Column D | Kwali comments left in blank template | Removed Kwali comments | 2018-09-12
15 | ST | BicycleSummary | E11,12,13 | Updated forumulas so that it outputs "--" if no pole-mounting space is identified. | updated in blank spreadsheet | 2018-09-12
15 | ST | FiatSummary | E11,12,13 | Updated forumulas so that it outputs "--" if no pole-mounting space is identified. | updated in blank spreadsheet | 2018-09-12
16 | ST | (E) Loads | AA | Updated all cells so that they have the correct drop down menu list. | updated in blank spreadsheet | 2018-09-13
16 | KR | (E ) Loads | Columns AJ to AU | Added the loads excluded in the "Bicycle Loads" and "Fiat Loads" tabs into the list of existing appliances not powered by PV system and made two different lists for the 2 designs - Bike and Fiat. |  | 2018-09-13
16 | KR | Site Info and Intermediate tabs | multiple | Made it so that the intermediate tabs allowed for more rooms. | done | 2018-09-13
17 | MH | BicycleSummary | multiple | Updated cells E11:E12 to reference column J. Updated cells I10:I12 to reference column D. | updated in blank spreadsheet, needs to be updated in all spreadsheets. | 2018-09-14
17 | MH | Fiat Summary | multiple | Updated cells E11:E12 to reference column K. Updated cells I10:I12 to reference column E. | updated in blank spreadsheet, needs to be updated in all spreadsheets. | 2018-09-14
17 | MH | Bicycle Loads and Fiat Loads | F5:F167 | Updated formulas in cells F5:F167 to only output bulb or tube: =IF('(E) Loads'!F5="","",IF(OR('(E) Loads'!AF5="bulb",'(E) Loads'!AF5="tube"),'(E) Loads'!AF5,"")) Updated formulas in cells F168:F326 to only output bulb or tube: =IF('(F) Loads'!F5="","",IF(OR('(F) Loads'!AB5="bulb",'(F) Loads'!AB5="tube"),'(F) Loads'!AB5,"")) | updated in blank spreadsheet, needs to be updated in any spreadsheet that has Fan,100 in the green output tab | 2018-09-14
18 | KR | (F) Loads | Columns AE, AL, AN | Loadsguide table reference only went down to row 33, needs to go down to 60 | Updated equations to make loads table be called down to row 60 | 2018-09-19
18 | KR | Fiat Loads | Table starting at Q437 | Was referencing the bicycle use profile the bicycle use profile from the (N) Loads Sans RL&F section instead of the fiat use profile. | done, and also checked the bicycle loads tab was correct. | 2018-09-19
18 | KR | Designs | J4, J5 | Someone had accidentally removed the pole mounting surface azimuth and tilt angles from the spreadsheet, so I put them back in as 180 and 10, respectively. | done | 2018-09-19
18 | KR | (N) Loads (Sans RL&F) | Column N | All new lighting was coming up as 10W power. So I changed =IF(F4="","",VLOOKUP(F4,'Loads Guide'!$G$6:$R$60,12,0)) to =IF(F4="","",IF(I4<>"",VLOOKUP(I4,'Site Info'!$E$4:$F$5,2,0),VLOOKUP(F4,'Loads Guide'!$G$6:$R$60,12,0))). | done | 2018-09-19
19 | MH | Loads Guide and Rec. Loads - research - Nigeria | Loads Guide P7:T7 and Rec Loads Q8:T8, V8 | Kristen and Meg decided to decrease the estimated power and duty cycle for refrigerators based on finding a number of refrigerators that seemed to have a rated daily energy consumption of 1.2 kWh and 130 W, which would correspond to a duty cycle of 39% or 9.3 hours of use per day. Also, based on the same specs (from a fridge at Tunga Adaka), we increased the max current to 1.3 A, which increased the surge factor to 2.2. These changes need to be made to the Loads Guide for all sites (and to avoid confusion, to the Rec Loads, but this won't impact any calculations). | done | 2018-09-24
20 | MH | Loads Guide and Rec. Loads - research - Nigeria | Loads Guide P7:R7 and Rec Loads Q8:R8, V9 | Kristen and Meg discussed fridges again and decided to use an estimate of 24 hours and adjust the power instead. Still based the average refrigerator on 1.2 kWh/day, which results in an average wattage of 50 W. Everyone with sites with existing or future refrigerators will need to adjust the wattage according to the kWh/day rating of the refrigerator. If the fridge has a power rating but does not have a kWh/day rating, assume a duty cycle of 39% and multiply the rated power by 0.39. | done in template, all spreadsheets with existing or future refrigerators will need to be updated. | 2018-09-26
21 | MH | Loads Guide and Rec. Loads - research - Nigeria | Multiple | Updated a number of the different assumptions including the medical appliances included in each design, the power rating for the remote monitoring system and the power rating for the suction machine | done | 2018-10-09
21 | MH | Bicycle Loads, Fiat Loads, Bicycle Summary, Fiat Summary | B4:B167 and column BO on loads tabs, column H on summary tab | Updated to output "~" if load was being replaced and to output the number of loads being replaced on the summary tabs | done | 2018-10-10
21 | MH | Site Info | C27:C47 | Added method to calculate roof size based on google earth images; allowed inputs from Olakunle spreadsheets and google earth | done | 2018-10-11
21 | MH | Assumptions | C6 | Changed inverter efficiency to 0.72 from 0.88. This was based on a conversation with Arne about the low capacity factor for the system. From a back-of-the-envelope analysis based on a 5 kW system, we found that the average inverter efficiency, weighted by energy use each hour, would be close to 64%-72%. | done | 2018-10-11
22 | MH/KVW | Site Info and Loads Guide |  | Kaileigh added a diagram for the Site Info tab and Meg changed the power value for remote monitoring to 10 W based on Scott's measurement of the Outback system. | done | 2018-10-12
23 | MH | Site Info | C26,35,44 | Changed default output of formula to 0. Otherwise the logic on the designs tab treated a blank cell as infinitely big and always said there was area available. | done - needs to be updated on any 10/12 designs | 2018-10-17
24 | KR | Loads Guide | R18-R21 and C17 | Changed "efficienct fan" power from 60W to 70W | done | 2018-11-15
24 | KR | Tilt Calculations | all | Updated tilt tabs so it's only 1 tab and it estimates the best surface azimuth angle for the perfect pole-mount location. | done | 2018-11-15
24 | KR | Site Info and Designs | Notes | Added notes: 0° is perfectly south-facing, 90° is perfectly east-facing, -90° is perfectly west-facing, -180° is perfectly north-facing (not +180° in this spreadsheet) | done | 2018-11-15
24 | KR | Solar Resource | Instructions | Updated instructions with Tom's | done | 2018-11-15
24 | KR | Solar Resource | Calling Solar Insolation data from Tilt Calc spreadsheet: Rows 10, 14, 18, 22 | -Updated where solar insolation is called from -No need for solar monthly solar insolation from the Tilt Calc spreadsheet, just the min month | done | 2018-11-15
24 | KR | Designs | J4, J5 | - Surface Azimuth angle auto populates - Made tilt angle cell color pink - Added notes by each | done | 2018-11-15
24 | KR | Bicycle Summary and Fiat Summary | I10, I11 | Changed W units to kW | done | 2018-11-15
25 | KR | FiatSummary | E13 | Changed '=IF('Site Info'!C45="no","--",Designs!K5) to =IF('Site Info'!C45="no","--",Designs!J5) Should have been changed in a prior version but must have been missed | done | 2018-11-16
25 | KR | FiatSummary and Bicycle Summary | E18 | Changed the tilt angle references from in the Site info tab to the new rows in the designs tab where the potentially new tilt angles reside | done | 2018-11-16
25 | KR | Solar Resource | Row 22 | Made the "Insolation incident on the specified tilted surface and surface azimuth angles and considering shading (kWh/m2/day)" be calced for the no-longer perfect space (since it is possible for the pole mount array to have shade) and now have the acutal monthly values be populated. | done | 2018-11-16
25 | KR | Tilt Calculations | B104 | Modified the dark pink boxes (for the pole mount array) to give the monthly solar radiation outputs instead of just the min month output | done | 2018-11-16
25 | KR | Tilt Calculations | Row 34 | Altered the roof-mounting calcs so that they optimize the tilt angle if the exisiting roof angle is below 10 degrees. | done | 2018-11-16
26 | TQ | SiteOverview, BicycleLoadsOut, FiatLoadsOut | Facility name | Centered the facility name | done | 2018-11-28
26 | TQ | SiteOverview, BicycleSummary, BicycleLoadsOut, FiatSummary, FiatLoadsOut | Facility type | If the country is Niger, change PHC to CSI 1 and CHC to CSI 2 in the output. | done | 2018-11-28
26 | TQ | Site Info | C8 | Add CEG to the drop-down for school type. | done | 2018-11-28
27 | KR | Loads Guide | Row 35 | Added satelite decoder to list of loads | done | 2018-12-07
27 | KR | Site Info | D19 | Changed instructions for filling out tilt angle so people won't put in 10 if it is less than 10 | done | 2018-12-07
27 | KR | Site Info | Bottom of sheet | Deleted the photo of a site that was accidentally left in there. | done | 2018-12-07
28 | TQ | BicycleSummary | K39 | Restored missing formula | done | 2018-12-11
28 | TQ | Designs | E19, E26 | Corrected formula so the tilt is displayed if PV space 2 or 3 is used in the Fiat but not the Bicycle. | done | 2018-12-12
29 | KR | (N) Loads (Sans RL&F) | Column O | Changed =IF($F4="","",IF($K4+$L4>M4,0,M4-$K4-$L4)) to =IF($F4="","",IF($K4>M4,0,M4-$K4)) In order to prevent future loads, such as security lights, from being excluded in the bicycle design | done | 2019-01-10
29 | KR | Light Green output tabs | General | Populated footer and went through Meg's printing email and formatted accordingly. The set print area will still need to be performed for every site individually. | done | 2019-01-10
30 | TQ | Light Green output tabs | General | Updated the AddFooterToAll macro so that it does not require interaction, and added a Workbook_BeforePrint handler so it will be called automatically when the document is printed. | done | 2019-01-16
31 | KR | Loads Guide | Rows 36 and 37 | Added DVD player from Kossoma site Fixed use profile from 1 hours to 0.33 hours (cells: AL36 to AN36) | done | 2019-01-17
31 | KR | (E) Loads | AJ5 | Added the red to formula: =IF(AND('Bicycle Loads'!C4<>"Exclude",OR(AI5="Included",AI5="",'Bicycle Loads'!C4="")),"",MAX(AJ$4:AJ4)+1) Otherwise, if first item in (E ) Loads was excluded, it wouldn't show up in list of excluded loads. | done | 2019-01-17
32 | TQ | Light Green output tabs |  | Adjusted borders, print area, and some column widths. | done | 2019-01-25
33 | MH | (E) Loads | BA111 | Cell had been overwritten with the value "50" since the 1/10 template. Copied formula down instead and checked all systems that used January templates to see if they were impacted - the change only affected Kurudu in Nigeria because most sites did not have 111 existing loads. | done | 2019-02-12
34 | KR | Vaccine Fridge VaccineSummary | -- | I added these two tabs | done | 2019-02-28
34 | KR | Assumptions | Rows 16, 18, 24 | I added efficiencies specific to DC vaccine fridge systems | done | 2019-02-28
35 | KR | Scale-Up | entire | Added worksheet to add information available to sites we didn't conduct full audits on, then that information is being pointed to by the other worksheets | done | 2019-08-11
36 | MH | Simplified | entire | Removed functionality to assess existing vs. future vs. replacement loads and include distinctions for bulbs vs tubes. Organized so inputs could be either pre-generated or manually entered. Reduced number of outputs to only show one scenario. Updated Loads Guide to match current "QA Framework". Updated load schedule to count the full power of a load if it is on during that hour and allowed user to choose in the assumptions whether to refer to the maximum power or maximum power based on the time of use load schedule. | done | 2021-02-03
37 | MH | Simplified v0.1 | entire | Made shading for all sites default to 100%, made color coding systematic and added instructions on each sheet, attempted to improve usability by adding default values. Updated formulas to automatically calculate tilt angle for pole mount and calculate angles greater than 40 degrees so spreadsheet would be more widely usable. Corrected two errors in "Tilt Calculations" tab which did not impact prior designs (number of days in months in formulas in column B and using "AGGREGATE" instead of "Max" to calculate maximum minimum monthly insulation while ignoring errors. This was an issue for arrays titled higher angles because the formulas begin to have errors at unreasonable tilt angles.) Locked all formulas and protected sheets (no password - just Unprotect to edit). | done | 2021-09-06
38 | MH | Simplified v1 | General Site Info | Made updates to instructions | done | 2022-03-20
39 | MH | Simplified v1.1 | Loads Guide | Added additional optional medical appliances listed in QA Framework to loads guide so they would appear in the dropdown menu. Also updated some instructions on the General Site Info and Loads tabs. | done | 2022-12-16

## Lit References (hidden)
VFXR3648A
|  |  |  | Derate Factors | Derate Value | Range of Accepted Values
|  |  |  | Module power tolerance | 0.95 | 0.80-1.05
|  |  |  | Inverter and transformer | 0.96 | 0.88-0.98 | SEI handbook had 0.96, but outback inverter is 93%
|  |  |  | Module Mismatch | 0.98 | 0.97-0.995
|  |  |  | Diodes and connections | 0.995 | 0.99-0.997
| Laptop computer |  |  | DC wiring | 0.98 | 0.97-0.99
| Desktop computer |  |  | AC wiring | 0.99 | 0.98-0.993
| Internet (V-Sat connection) |  |  | Soiling | 0.95 | 0.30-0.995
| Printer, ink jet |  |  | System downtime | 0.98 | 0.00-0.995
| Printer, laser |  |  | Shading | 0.9 | 0.00-1.00
| VHF radio receiver: Standby |  |  | Overall dc-to-ac derate factor | 0.72293
VHF radio receiver: Transmitting
Refigerator for staff
Portable air conditioner
Portable electric space heater
Water purifier (UV)
Water purifier (reverse osmosis/other water purifier)
Micro-nebulizer
| Nebulizer | 85
| Oxygen concentrator | 290
| Pulse oximeter | 50
For each of the 15 sites (plus a few “buffer” sites), SERC will prepare the following elements. These will be shared with the Financial Consultant to help with their analysis and to enable them to solicit a choice of designs from the facilities:
· Summary of the existing situation of the facility
· Summary of loads and assumptions
· Drawings showing options for installations
· Sizing of main components
· Expected power and surface area of array
· One-line diagram

## Rec. Loads - Research - Nigeria (hidden)
| Background Research References: Minimum Requirement of Health Centers in Nigeria (Source: National Primary Healthcare Development Agency (NPHCDA, 2015)) System Design Report, UNF Sustainable Solar Solutions For Health Facilities - Ghana, Solar Electric Light Fund and Power World Ltd., 2017 Photovoltaic systems for use in individual homes, schools and clinics, South African National Standard, NRS 052-1:2012 Access to Modern Energy Services for Health Facilities in Resource-Constrained Settings, WHO 2014 Initial Surveys (Sept 2017, n = 60) and Detailed Audits (Nov 2017- Feb 2018, n = 11) conducted by SERC staff in Nigeria | [10 empty] | Recommended Loads If a site does not already include in the existing or future loads the recommended number of items listed in column N, add the items to the list of loads for the site. If a site lists a future load, but does not specify the desired hours of use and/or power, the values in columns O and P can be used.
Basic Load | Required by government | Rec. by UNF / SELF Ghana designs | Rec. by South African Standards | WHO power rating | Number of facilites that have appliance in detailed audits (out of 8 PHC & 3 CHC) | Number of appliance found in a facility | Use Pattern (initial surveys + research) | Range of Hours of Use (initial surveys + research) | Range of Hours of Use - including desired hours of use (Detailed audits) | Range of Power (initial surveys + research) (W) | Range of power (Detailed audits) (W) | Number of Units to include in designs for PHC | Number of Units to include in designs for CHC | Hours of Use for Designs | Power Draw for Designs (W) | Max current demand (A) | Surge factor | Power factor | Logic behind selection | Additional work required | UNF comments | Comments from ECREEE meetings | Comments from Gopal at Clinton Health Access Initiative
General Applinces/Equipments
Airconditioner | No | No | No | 1000 - 1500 W | 1 CHC | 3 |  |  | 6-10 |  | 1500 | -- | -- | -- | -- | -- | -- | 0.95 | Project team decided to not include air conditioners in the PV design loads due to high wattage demand. Kwali has three existing airconditioners and plans to add 4 more - these would not be supported by the solar system and need to run off an alternate system. | Identify appropriate power factors for all loads and identify appropriate surge currents for loads highlighted in orange. | Agreed | Agreed
Computer (laptop) | CHC | Yes, 150 W for 6 hours, PF0.8 | Yes, 6 hours | 15-200 W desktop, 20-60 W laptop | 1 PHC, 1 CHC | 1 |  | 5 to 18 | 0-5 | 60 to100 | 65-100 | 1 | 1 | 6 | 60 | 0.27273 | 1 | 0.7 | UNF and SA recommend sites have a computer and they were seen in both PHC and CHC sites, so we recommend including 1 in each site design. The power draw is based on the maximum power for a laptop and the hours of use are based on the UNF and SA recommendations. |  | I would always steer the clinics to laptops, given the much lower power consumption (incl for use in staff quarters) compared to desktops, which tend to have a high surge power as well when starting up | Size for a laptop
Fan | No | Yes, 75 W for 8 hours, PF0.8 | No | 30 - 100 W | 7 PHC, 3 CHC | 3-25 |  | 4 to 12 | 4-12 | 25 to 100 | 18-100 | Based on room size: 0 - 100 m^3: 1 fan 101- 200 m^3: 2 fans 201-300 m^3: 3 fans (essentially 1 fan per 100 m^3) Exclude certain rooms - see notes | Same as PHC | 8 h, except rooms with beds: 12 hours | 60 | 0.27273 | 1.1 | 0.9 | The power rating of fans found during the fieldwork is 70 - 100W, but there are energy efficient fans of 50 - 60 W that could be installed as replacements. Will need to decide whether it is worth replacing 70 W fans. 100 W fans should be replaced. The number of fans was estimated looking at data from the audited sites and comparing the room size to the number of fans. There was not a clear trend, but it did seem that some sites started to add a second fan when the size of the room exceeded 60 cubic meters and rooms above 100 cubic meters have 2 fans. Currently, we are proposing including fans in rooms that do not already have the recommended circulation. Rooms that should not have fans added: toilet, kitchen, lab, hallway, entry, storage. |  | Design option: put some fans on a timer (e.g. max 1 hour) so that at least the fan needs to be turned on/off manually every hour; this would be practical in certain rooms which are not occupied at night. | 10 hours is realistic, but could reduce
General Purpose Refrigerator/Freezer | PHC, CHC | Yes, 85 W for 12 hours, PF1 | No | 150 - 200 W | 2 PHC, 3 CHC | 1,1,1,4,6 (4 unused in the storage room) |  | 24 | 8 - 24 | 125 to 300 | 30-250 | 1 | 1 | 24 | 50 | 1.3 | 5.72 | 0.65 | General purpose refrigerators were found in 5 facilities. The most common size was 65 W, but these were DC. The largest power estimate we saw was 135 W, but we commonly saw energy ratings of 1.2 kWh/day and 0.5 kWh/day in our sites and in online searches. We based the recommended power on a large refrigerator at Tunga Adaka with a nameplate value of 1.2 kWh/day. We divided this by 24 hours to get the average power. (The rated power was 130 W, whcih suggests a 38.5% duty cycle). The amperage was based on the maximum current of 1.3 from the same label. Proposal: include both a general purpose fridge/freezer in our list of loads and assume that the general purpose fridge could be used for blood storage if needed. If a site does not have a vaccine refrigerator, we would not include it as a load on our system, assuming that the vaccine refrigerator would need to be powered separately and will likely be supplied with a solar power system when the refrigerator is supplied. If a site has a functioning vaccine refrigerator, we would leave it as is. If a site has a vaccine refrigerator, but can't power it, we should provide power, either through a prioritized circuit or a separate system. |  |  | Include, but do not include vaccine refrigerator
Internet Router | CHC | No | No | 85 - 500 W (V-Sat connection) | 1 PHC | 2 |  | 24 | 24 |  | 40 | 1 | 1 | 24 | 2.5 | 0.011364 | 1 | 0.7 | We decided a USB pen-drive style modem should be included with the system, though we aren't sure of the power for one of these, but are currently estimating it at .5 A * 5 V = 2.5 W |  | Our remote monitoring systems do have a router to be able to connect wirelessly to a cloud-based system. The standard OpticsRE (Outback) system stores data on a SD card which would need to be retrieved manually on-site. The modem allows the system to connect to the cloud and allows for 'remote' monitoring where the cell phone network allows for it (typically a simple 2G signal is sufficient). From experience, cell phone network can be completely absent only in the most remote areas (Ghana, Uganda) or actually in most rural areas (Liberia); the latter may require power for an HF radio (approx 130W when broadcasting). Applicable to Niger context perhaps? Similarly, depending on the state of the HMIS system in-country, an internet connection (and thus router) may be useful so that indicators can be uploaded directly to the information system rather than having to be written down in a ledger, collected regularly, and then uploaded to the system at a more centralized location with an internet connection. With e-health / m-health on the rise, I would keep a router for internet and comms purposes on the energy budget. | Make sure to include internet access for the laptop (like a pen drive)
Lighting (interior) | HP, PHC, CHC | Yes, 8 W for 5 hours, PF0.8 | Yes | 5 - 13 W (70 - 90 lm/W) Recommend ~ 162 lux/m^2 | 6 PHC, 3 CHC | 14-60 |  | 12 | 2-13 | 5 to 60 | 13-70 | based on size of rooms (162 lm/m^2) lower requirement for other rooms? | Same as PHC | 18 hours for rooms without windows 6 hours for rooms with windows 2 hours for bathrooms, storage and low use rooms | 10 | 0.045455 | 1 | 0.7 | Assumes a 60 W incandescent equivalent if incandescent efficacy is 15 lm/ W and LED efficacy is 90 lm/W. 162 lm/m^2 requirement comes from WHO report and appears to be consistent with findings in the field. May decide to use a lower lumens / m2 requirement for non-examination rooms. |  |  | Refine site-by-site. Max lighting in a few rooms, less in others. Fewer hours in rooms with windows and very few hours in bathrooms and storage.
Lighting (outdoor/security) | No | Yes, 8 W for 12 hours, 0.8 PF | Yes | 10 - 100 W | 6 PHC, 3 CHC | 3-19 |  |  | 2-24 |  | 13-60 | 4 per building (1 per side) | Same as PHC | 10 | 10 | 0.045455 | 1 | 0.7 | Estimate of number of lights assumes that each side of the building will have 1 light |  | One per side of the building could be sufficient, though it will depend on the brightness and the directionality of the light to ensure that the compound is sufficiently lit at night. | Change to 1 per side and 10 hours, on light sensitive timers
Lighting (Task - angle poise lamp) | CHC | Yes, 50 W for 2 hours, PF0.8 | No | -- | -- | -- | [5 empty] | 1 | 2 | 4 | 50 | 0.22727 | 1 | 0.7 | Angle lamp quoted in UNF work was for an LED lamp with 20,000lx at 0.1 m, estimated at 50 W. Recommend 1 for PHC and 2 for CHC. |  |  | Reduce the number of hours - 2 hours/ birth/day
Mobile Phones | HP, PHC, CHC | Yes, 5 phones at 5 W for 3 hours, PF0.8 | No | 5 - 20 W | -- | -- |  | 24 |  |  |  | 1 per staff member | Same as PHC | 1 | 10 | 0.045455 | 1 | 0.7 | We assume staff will be charging 1 h / day and restricting use by outlets for patients/neighbors. We are assuming for the worst case scenario where all these phones are plugged in at one time over 1 hour. |  |  | Change to 1 per staff
Printer | No | Yes, 150 W for 2 hours, PF0.8 | Yes (copier), 4 hours | 65 - 100 W for ink jet | -- | -- | [5 empty] | -- | -- | -- | 100 | 0.45455 | 1 | 0.7 | Ink jets are more common; WHO lists 65- 100 W for an ink jet printer; assumed to be used 2 hours per day (from UNF estimates). UNF and SA both included printer/copier in loads for health clinics. |  |  | Remove (ECREEE does not see the need and does not want the health center to become a printing shop/charging station)
Remote Monitoring Platform for Solar System | No | Yes, but not listed as a load | No | -- | -- | -- | [5 empty] | 1 | 1 | 24 | 5 | 0.045455 | 1 | 0.7 | This website says the remote monitoring requires 1 W: http://www.poweringhealth.org/index.php/topics/technology/remote-monitoring Power draw might be similar to a wireless router. It seems like there is a range of depending on the router (2-20 W). This is an odd website, but they have user submitted data for a few different routers: http://www.tpcdb.com/list.php?type=11 |  | As mentioned above (router) the charge controller will log the data real-time; this is indeed not listed as a separate load and it's unclear what the 'losses' are compared to a charge controller where the MATE3 system is disabled. The load will be the router/modem to connect to the cloud-based system and upload data / download instructions.
Television | No | Yes, 150 W for 4 hours (staff quarters), PF0.8 | Yes, sort of (wall-mounted SSO for educational equipment) | -- | 2 PHC | 1-8 |  | 4 to 12 | 2-12 | 40 to 90 | 80-90 | 1 per staff room | 1 per staff room | 6 | 90 | 0.40909 | 1 | 0.7 | Chose high end of observed television power consumption and assumed high end of stated hours of use. est.use h: 2, 6h and desired use h: 8,12. UNF and SA included TV in their loads |  | You could go for a much lower power consumption, depending on what is available on the market with solar home system providers (as low as 10-50W); more unlikely to find efficient appliances in Niger though. | Only include television if staff quarters are included. Make sure staff quarters are on separate system, lower priority circuit or load limted.
Telephone (RT Com) | PHC, CHC | No | No | 2 W standby, 30 W transmitting ( VHF radio) | -- | -- |  | 24 |  | 40 |  | -- | -- |  | 40 | 0.18182 | 1 | 0.7 | Decided not to include given that only one site was found with a working RT Com, and most sites said they used their mobile phones instead. Would recommend for sites without mobile phone network. |  | See comment above re HF (more applicable for long-distances and contacting referral hospital and ambulances) and VHF.
Medical Appliances
Abacus 380 (Hematology machine for full blood count) | No | No | No | 230 - 400 W | -- | -- | Used 4 h on HIV screening day and 1 h on another day of the week |  |  |  |  | -- | -- | 4 | 400 | 1.8182 | 1 | 0.9 | Only found during initial survey at a few sites; may not need to be required. Power draw from WHO report is 230 - 400 W.
Autoclave / Sterilization Machine | PHC, CHC | No | No | 2000 - 6000 W | 1 PHC, 1 CHC | 1 |  | 2 | 2-8 | 1200 to 2850 | 1600-1605 (and one site in Niger had a 1050 W autoclave that was not in use) | -- | -- | -- | -- | -- | -- | -- | Required by government, but our project team decided to not include autoclaves in the PV design loads given the high power draw. Sites said that as an alternative, they typically use wood, kerosene or gas to heat an "autoclave stove". We investigated the possibility of including UV sterilizers, but found that they are not effective as a stand-alone device for sterilization. |  | We are currently investigating whether or not we could power up an autoclave (e.g. a 1500W device) under certain conditions. E.g. with a fully charged system, we may be able to power up an autoclave for an hour in the afternoon (when batteries are fully charged and we have surplus power available). We will be testing a few autoclaves to review the actual load profiles (doubtful to be 1500W across the entire hour) to get a clearer idea of what the energy consumption would be like over an hour.
Blender and mill | CHC | No | No | 1400 W (autoclave grinder) | -- | -- | [5 empty] | -- | -- | -- | -- | -- | -- | -- | Government requires, but we did not find these in any sites; considering not requiring | Look more into what this is used for so we have a better idea of how many to have, power, use hours, etc? Could this be manual? Called Dutse Alaji, Kabi Mangoro, Ibwa 1: sites did not think this was necessary. Jimento will call a few more to confirm.
Bloodbank Refrigerator | no | No | No | -- | 1 PHC, 1 CHC | 1 |  |  | 7-24 |  | 135 | -- | -- | 14.4 | 135 | 0.82 | 1.3363 | 0.65 | We are assuming a blood storage refrigerator requires the same energy as a general purpose refrigerator, but accounting for only 1 general refrigerator and 1 vaccine refrigerator per site (unless sites already have additional refrigerators).
Cd4 Machine for HIV | No | Yes, HC only. 80 W for 4 hours, PF0.8 | No | 200 W | -- | -- | Used once a week for 5-6 h | 5 to 6 |  | 200 |  | -- | -- | 5 | 200 | 0.90909 | 1 | 0.9 | Not seen in detailed audits. WHO says 200 W, UNF says 80 W for 4 hours. |  | I believe these were only available in HC III in Uganda, and not in (lower-tier) health facilities in Ghana (type CHPS).
Centrifuge | CHC | Yes, HC only. 250 W for 1 hour, PF1 | No | 250 - 400 W | 1 PHC, 2 CHC | 1 |  | 2 | 2-12 |  | 100-110 | -- | 1 | 2 | 110 | 0.5 | 1 | 0.9 | 3 sites have centrifuges: 100, 110, 110; government requires for CHC and UNF included for HC. with est.use h: 0, 2, 8h and desired use h: 2,2,12. We assume the 8/12 h estimates is not realistic, e.g. includes downtime. => go with higher power for existing centrifuges: 110W => go with more popular/more realistic use hours: 2 h |  | Agreed | Ask why UNF had estimated this as 1 hour - should we reduce?
Chemistry Machine (Raflatron) | No | No | No | 45 - 88 W | -- | -- | Used once a week for 2-4 h | 2 to 4 |  |  |  | -- | -- | 4 | 88 | 0.4 | 1 | 0.9 | Only found during initial survey at a few sites; may not need to be required.
Electric Microscope(Bright field white light) | CHC | Yes, HC only. 60 W for 4 hours, PF0.8 | No | 20 - 30 W | 2 PHC | 1 |  | 2 to 3 | 2-12 | 20 to 30 | 15-30 | -- | 1 | 2 | 30 | 0.13636 | 1 | 0.7 | 2 sites have microscopes: 15, 30W; government requires for CHC and UNF included for HC. only one site supplied estimated hours of use: est.use h: 0 h and desired use h: 2 h. => go with higher power for existing microscope: 30W => go with the only use hour stated, which we think is reasonable: 2 h |  | Agreed
Electrophoresis Genotype Machine | No | No | No | 190 W (GeneXpert MTB/RIF diagnostic) | -- | -- |  | 3 |  |  |  | -- | -- | 3 | 190 | 0.86364 | 1 | 0.9 | Power based on WHO estimate and hours based on initial audit
Hot Oven | No | No | No | 500 - 1560 W (dry heat sterilizer) | -- | -- | Used 1-2 h a week | 1 to 2 |  |  |  | -- | -- | 2 | 1000 | 4.5455 | 1 | 1 | Only found during initial survey at a few sites; may not need to be required and may want to disallow. | Decide if we should prohibit the use of these due to their high power.
Oxygen Concentrator | No | Yes, HC only. 350 W for 4 hours, PF1 | No | 270 - 310 W or 70 W | 1 CHC | 1 |  |  | 2-12 |  | 10 | 1 | 1 | 4 | 310 | 1.4091 | 1 | 0.9 | Chose highest value from WHO power ratings and average usage from UNF work. Recommend for CHC based on UNF work and presence in 1 CHC clinic. Still need to determine appropriate power value. |  | Agreed, and commonly quoted as a medical appliance that is often missing but with a high impact/value. | Mr. Seini recommended including for PHC as well. Thought the power estimate was high and ones seen in Niger were lower power. | Regarding your other question about a load estimate for oxygen concentrators, my colleagues recommended going with 350W. The number of hours per day of usage is a complicating factor though: if there is a patient who needs medical oxygen, the concentrator will need to run 24 hours a day until the patient is well enough to be taken off the oxygen supply. This is likely to significantly increase the sizing of the solar power system. This — and the need for recurring, reliable maintenance — is a major reason for CHAI being on the fence about oxygen concentrators’ feasibility in low-resource settings, barring for niche applications. MH: This website suggests oxygen concentrators range between 20 W – 600 W.
Photoelectric Colorimeter | No | No | No | -- | 1 CHC | 1 | Used once a week for 2-4 h | 2 to 4 | 2-8 | 11 | 11 | -- | -- | 4 | 11 | 0.05 | 1 | 0.9 | Found in use in CHC clinic, but not required by other organizations. |  | Not seen in UG or GH, but low power consumption so reasonable to allow.
Phototherapy device | [11 empty] | -- | ? | 24 | 80 | 0.36364 | 1 | 0.7
Solar Vaccine Refrigerator | HP, CHC | Yes, 85 W for 12 hours, PF1 | Yes | 115 W | 3 PHC, 2 CHC | 1 - 2 |  | 24 | 6-24 | 65 to 370 | 36-130 | -- | -- | 24 | 81.25 | 0.59091 | 1.6 | 0.65 | See discussion above under "General refrigerator/freezer" regarding vaccine refrigerators. 5 sites had vaccine refigeration: 65, 65, (waiting for accurate data from Kwali), 120, 130W They should be on for 24 h, but with a duty cycle => go with higher power for existing fridges: 130W Jimento indicates this is a popular fridge seen in the field: https://www.bmedicalsystems.com/en/product/tcw-2000-ac/: 1.87 KWh at +43°C (Freezer OFF), 1.95 KWh at +43°C (Freezer ON). With the freezer off, this is equivalent to a 130 W refrigerator operating at a 60% duty cycle. This corresponds to the duty cycle quoted by GE: http://products.geappliances.com/appliance/gea-support-search-content?contentId=16932 |  | Side note: are there any direct drive fridges? Are fridges recommended to be on their own separate independent circuit (or power system) to remain WHO certified? Are most fridges gas/power? Are they DC/AC, and if so would they require a DC to AC converter to be connected to a centralized power system? | Discuss with UNF - perhaps leave out of the scope of our systems. | Confirmed that vaccine refrigerators must be on their own system or must be approved as part of an "energy harvesting" system. Provided WHO standards: http://apps.who.int/immunization_standards/vaccine_quality/pqs_catalogue/catdocumentation.aspx?id_cat=17 http://apps.who.int/immunization_standards/vaccine_quality/pqs_catalogue/catdocumentation.aspx?id_cat=36
Suction Machine | PHC, CHC | Yes, HC only. 590 W for 5 hours, PF1 | No | 90 - 200 W or 33 W | -- | -- |  |  |  |  | In Niger, 3 sites had suction machines; 2 were 95 W and one was 184 VA | -- | 1 | 5 | 185 | 0.84091 | 1 | 0.9 | Decided to include for CHC given that the government requires, UNF included for larger sites and the health centers we talked to said they would want an electric one. Used power estimates from largest apparatus found in Niger | Look into gov't requirement - are they talking about the manual ones? Jimento called sites and said they typically use a manual one, but would prefer an electric one. Jimento to call Pandaji to ask about wattage of suction machine in storage. | Agreed
Water Bath | No | No | No | -- | 1 CHC | 1 |  | 2 | 2-8 | 851 | 851 | -- | -- | 2 | 851 | 3.8682 | 1 | 1 | Only found during initial survey at a few sites; may not need to be required and may want to disallow. | Decide if we should prohibit the use of these due to their high power.
| Abbreviations: | [12 empty] | Sum of power for medical appliances we are not including, but also not prohibiting (W): | 678
| PHC: Primary Health Care Center (Nigeria) | [12 empty] | Sum of daily energy for medical appliances we are not including, but also not prohibiting (Wh): | 2522
CHC: Comprehensive Health Care Center (Nigeria)
HC: Health Center (this seems to be the Ugandan equivalent of a CHC)
These are some other devices/services worth considering (recommended by Luc Severi at UNF)
| Power Consumption | Hours of use/day
Water pumping | 200 - 1000 W
Pulse oximeter (battery operated) | 50 W
Fetal heart monitors / doppler | 3 W | 2
Portable ultrasound machines | 6 - 28 W | 1
Patient Monitor for Vital Signs Measurements (e.g. NiBP, SpO2, HR, RR, EtCO2 and ECG) | 300 W | 24
Anesthesia machines (for CHC only) | 500 W - 1500 W | 2
CHAI in Nigeria recommended also including energy for a photo therapy device | Notes from Meg: The WHO "Access to Modern Energy Services" document suggests 440 W ( in Table 3 on page 24), while I found two other suggested estimates of 50 - 80 W from this paper (which references this LED device). We did not see any of these in our site audits (even at sites that had grid connections), so I'm not sure what is reasonable to assume for Nigeria. Also, it looks like the duration of treatment is 24 - 48 hours, which then may raise the same questions for this device as for the oxygen concentrator.
Note on C2: Jem Porcaro: Suggest you also look at: http://www.who.int/medical_devices/md_maternal_BOOK_May2016_D.pdf Only downside is that the publication doesn't identify which devices rely on power.
Note on S3: mjh80: I divided the wattage by 220 V to get a maximum amperage. This should be appropriate for most loads, but ones where this may be underestimating the surge current are highlighted orange for discussion,
Note on U3: mjh80: I haven't found a good source for this. UNF/SELF chose 0.8 for electronic loads and 1 for heating/motor loads (which is appropriate for resistive heaters, but not motors). Other sources: http://www.electrical-installation.org/enwiki/Practical_values_of_power_factor https://aceee.org/files/proceedings/2014/data/papers/9-959.pdf https://www.energystar.gov/products/lighting_fans/light_bulbs/key_product_criteria Additional sources identified by Jimento: http://www.saifurrahman.org/wp-content/uploads/2014/12/Load-Profiles-of-Selected-Household-Appliances-2.pdf https://www.slideshare.net/munthear/power-factor-44106896 https://www.sasta.co.za/wp-content/uploads/Proceedings/1950s/1953_Perk_Centrifugal%20Machines.pdf
Note on U7: mjh80: From Olakunle's measurement of fans
Note on U8: mjh80: newer refrigerators may have a PF of .9 or better
Note on U10: mjh80: We may want to also set a minimum power factor in addition to the minimum efficacy. An uncorrected LED can have PF as low as 0.3.
Note on B11: mjh80: This is stragely labeled as task/security in our spreadsheets, but all entries were for outdoor lights)
Note on S15: Windows User: used a higher power (10 W) for the max current draw as standby power is likely lower
Note on H20: mjh80: This is "waste autoclave or microwave" at Damangaza that has never been used and an autoclave at New Karishi that they say is used 8 hours per day.

## Tilt Calculations (hidden)
THE INPUTS
| Latitude (°) | Missing
Average Monthly reflectance factor (ρg)
| Jan | Feb | Mar | Apr | May | June | July | Aug | Sep | Oct | Nov | Dec
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Average Montly Insolation (kWh/m2/day)
| Jan | Feb | Mar | Apr | May | June | July | Aug | Sep | Oct | Nov | Dec
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note Constant(s):
| Gsc (W/m2) | 1367
PRE CALCULATIONS
|  | n | declination (б) | ωs | Gon (W/m2) | daily X-tra Insolation (Ho) (J/m2/day) | Inputed Ave Monthly Insolation (Ĥ) (kWh/m2/day) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | Inputed Ave Monthly reflectance factor (ρg) | Kt bar | first Hd/H bar | second Hd/H bar | rightful Hd/H bar | Hd bar (J/m2) | Hb bar (J/m2)
| Jan | 17 | -20.917 | #VALUE! | 1410.1931 | #VALUE! | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Feb | 47 | -12.9546 | #VALUE! | 1398.1344 | #VALUE! | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Mar | 75 | -2.4177 | #VALUE! | 1379.455 | #VALUE! | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Apr | 105 | 9.4149 | #VALUE! | 1356.4219 | #VALUE! | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| May | 135 | 18.7919 | #VALUE! | 1336.1477 | #VALUE! | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| June | 162 | 23.0859 | #VALUE! | 1324.6689 | #VALUE! | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| July | 198 | 21.1837 | #VALUE! | 1323.4853 | #VALUE! | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Aug | 228 | 13.455 | #VALUE! | 1335.0331 | #VALUE! | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Sept | 258 | 2.2169 | #VALUE! | 1354.9186 | #VALUE! | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Oct | 288 | -9.5994 | #VALUE! | 1377.9552 | #VALUE! | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Nov | 318 | -18.912 | #VALUE! | 1398.1344 | #VALUE! | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Dec | 344 | -23.0496 | #VALUE! | 1409.1954 | #VALUE! | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Klein & Theilacker Method
The light pink and blue tables below are for determining the monthly energy for roof-mounted systems
Note: for roof mounts, we are only adding tilt if the exisiting roof is shallower that 10 degrees, and in which case we use the optimum tilt for the exisiting surface azimuth angle. If the roof has slope greater than 10 degrees, we use that slope for the module tilt, i.e. we do not add any racking to increase or decrease the tilt.
| Average Montly Insolation (kWh/m2/day) Jan: Identified PV Space: | [14 empty] | Minimum Monthly HT bar: | #VALUE! | [25 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE!
[27 empty] | Corresponding tilt angle: | 10 | [25 empty] | 11 | [24 empty] | 12 | [24 empty] | 13 | [24 empty] | 14 | [24 empty] | 15 | [24 empty] | 16 | [24 empty] | 17 | [24 empty] | 18 | [24 empty] | 19 | [24 empty] | 20 | [24 empty] | 21 | [24 empty] | 22 | [24 empty] | 23 | [24 empty] | 24 | [24 empty] | 25 | [24 empty] | 26 | [24 empty] | 27 | [24 empty] | 28 | [24 empty] | 29 | [24 empty] | 30 | [24 empty] | 31 | [24 empty] | 32 | [24 empty] | 33 | [24 empty] | 34 | [24 empty] | 35 | [24 empty] | 36 | [24 empty] | 37 | [24 empty] | 38 | [24 empty] | 39 | [24 empty] | 40 | [24 empty] | 41 | [24 empty] | 42 | [24 empty] | 43 | [24 empty] | 44 | [24 empty] | 45 | [24 empty] | 46 | [24 empty] | 47 | [24 empty] | 48 | [24 empty] | 49 | [24 empty] | 50 | [24 empty] | 51 | [24 empty] | 52 | [24 empty] | 53 | [24 empty] | 54 | [24 empty] | 55 | [24 empty] | 56 | [24 empty] | 57 | [24 empty] | 58 | [24 empty] | 59 | [24 empty] | 60
[27 empty] | Max Minimum Monthly HT bar over tilt angles: | 0
| Average Montly Insolation (kWh/m2/day) June: Exisiting roof tilt angle (°):; Average Montly Insolation (kWh/m2/day) July: 0 | [14 empty] | Corresponding tilt angle to Max Minimum Monthly HT bar over tilt angles: | #N/A
| Average Montly Insolation (kWh/m2/day) Jan: Output; Average Montly Insolation (kWh/m2/day) June: surface azimuth angle (°):; Average Montly Insolation (kWh/m2/day) July: 0 | [19 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0
| Average Montly Insolation (kWh/m2/day) June: tilt angle (°):; Average Montly Insolation (kWh/m2/day) July: 10 | [19 empty] | tilt angle (°): | 11 | [23 empty] | tilt angle (°): | 12 | [23 empty] | tilt angle (°): | 13 | [23 empty] | tilt angle (°): | 14 | [23 empty] | tilt angle (°): | 15 | [23 empty] | tilt angle (°): | 16 | [23 empty] | tilt angle (°): | 17 | [23 empty] | tilt angle (°): | 18 | [23 empty] | tilt angle (°): | 19 | [23 empty] | tilt angle (°): | 20 | [23 empty] | tilt angle (°): | 21 | [23 empty] | tilt angle (°): | 22 | [23 empty] | tilt angle (°): | 23 | [23 empty] | tilt angle (°): | 24 | [23 empty] | tilt angle (°): | 25 | [23 empty] | tilt angle (°): | 26 | [23 empty] | tilt angle (°): | 27 | [23 empty] | tilt angle (°): | 28 | [23 empty] | tilt angle (°): | 29 | [23 empty] | tilt angle (°): | 30 | [23 empty] | tilt angle (°): | 31 | [23 empty] | tilt angle (°): | 32 | [23 empty] | tilt angle (°): | 33 | [23 empty] | tilt angle (°): | 34 | [23 empty] | tilt angle (°): | 35 | [23 empty] | tilt angle (°): | 36 | [23 empty] | tilt angle (°): | 37 | [23 empty] | tilt angle (°): | 38 | [23 empty] | tilt angle (°): | 39 | [23 empty] | tilt angle (°): | 40 | [23 empty] | tilt angle (°): | 41 | [23 empty] | tilt angle (°): | 42 | [23 empty] | tilt angle (°): | 43 | [23 empty] | tilt angle (°): | 44 | [23 empty] | tilt angle (°): | 45 | [23 empty] | tilt angle (°): | 46 | [23 empty] | tilt angle (°): | 47 | [23 empty] | tilt angle (°): | 48 | [23 empty] | tilt angle (°): | 49 | [23 empty] | tilt angle (°): | 50 | [23 empty] | tilt angle (°): | 51 | [23 empty] | tilt angle (°): | 52 | [23 empty] | tilt angle (°): | 53 | [23 empty] | tilt angle (°): | 54 | [23 empty] | tilt angle (°): | 55 | [23 empty] | tilt angle (°): | 56 | [23 empty] | tilt angle (°): | 57 | [23 empty] | tilt angle (°): | 58 | [23 empty] | tilt angle (°): | 59 | [23 empty] | tilt angle (°): | 60
| Monthly kWh/m2 | Tilt Angle (°) |  |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
| #N/A | #N/A |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sep | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jun | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jul | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sep | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jun | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jul | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sep | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jun | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jul | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sep | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jun | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jul | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sep | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Identified PV Space: | [25 empty] | Minimum Monthly HT bar: | #VALUE! | [25 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE!
[27 empty] | Corresponding tilt angle: | 10 | [25 empty] | 11 | [24 empty] | 12 | [24 empty] | 13 | [24 empty] | 14 | [24 empty] | 15 | [24 empty] | 16 | [24 empty] | 17 | [24 empty] | 18 | [24 empty] | 19 | [24 empty] | 20 | [24 empty] | 21 | [24 empty] | 22 | [24 empty] | 23 | [24 empty] | 24 | [24 empty] | 25 | [24 empty] | 26 | [24 empty] | 27 | [24 empty] | 28 | [24 empty] | 29 | [24 empty] | 30 | [24 empty] | 31 | [24 empty] | 32 | [24 empty] | 33 | [24 empty] | 34 | [24 empty] | 35 | [24 empty] | 36 | [24 empty] | 37 | [24 empty] | 38 | [24 empty] | 39 | [24 empty] | 40 | [24 empty] | 41 | [24 empty] | 42 | [24 empty] | 43 | [24 empty] | 44 | [24 empty] | 45 | [24 empty] | 46 | [24 empty] | 47 | [24 empty] | 48 | [24 empty] | 49 | [24 empty] | 50 | [24 empty] | 51 | [24 empty] | 52 | [24 empty] | 53 | [24 empty] | 54 | [24 empty] | 55 | [24 empty] | 56 | [24 empty] | 57 | [24 empty] | 58 | [24 empty] | 59 | [24 empty] | 60
[27 empty] | Max Minimum Monthly HT bar over tilt angles: | 0
[6 empty] | Exisiting roof tilt angle (°): | 0 | [19 empty] | Corresponding tilt angle to Max Minimum Monthly HT bar over tilt angles: | #N/A
| Output |  |  |  |  | surface azimuth angle (°): | 0 | [24 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0
[6 empty] | tilt angle (°): | 10 | [24 empty] | tilt angle (°): | 11 | [23 empty] | tilt angle (°): | 12 | [23 empty] | tilt angle (°): | 13 | [23 empty] | tilt angle (°): | 14 | [23 empty] | tilt angle (°): | 15 | [23 empty] | tilt angle (°): | 16 | [23 empty] | tilt angle (°): | 17 | [23 empty] | tilt angle (°): | 18 | [23 empty] | tilt angle (°): | 19 | [23 empty] | tilt angle (°): | 20 | [23 empty] | tilt angle (°): | 21 | [23 empty] | tilt angle (°): | 22 | [23 empty] | tilt angle (°): | 23 | [23 empty] | tilt angle (°): | 24 | [23 empty] | tilt angle (°): | 25 | [23 empty] | tilt angle (°): | 26 | [23 empty] | tilt angle (°): | 27 | [23 empty] | tilt angle (°): | 28 | [23 empty] | tilt angle (°): | 29 | [23 empty] | tilt angle (°): | 30 | [23 empty] | tilt angle (°): | 31 | [23 empty] | tilt angle (°): | 32 | [23 empty] | tilt angle (°): | 33 | [23 empty] | tilt angle (°): | 34 | [23 empty] | tilt angle (°): | 35 | [23 empty] | tilt angle (°): | 36 | [23 empty] | tilt angle (°): | 37 | [23 empty] | tilt angle (°): | 38 | [23 empty] | tilt angle (°): | 39 | [23 empty] | tilt angle (°): | 40 | [23 empty] | tilt angle (°): | 41 | [23 empty] | tilt angle (°): | 42 | [23 empty] | tilt angle (°): | 43 | [23 empty] | tilt angle (°): | 44 | [23 empty] | tilt angle (°): | 45 | [23 empty] | tilt angle (°): | 46 | [23 empty] | tilt angle (°): | 47 | [23 empty] | tilt angle (°): | 48 | [23 empty] | tilt angle (°): | 49 | [23 empty] | tilt angle (°): | 50 | [23 empty] | tilt angle (°): | 51 | [23 empty] | tilt angle (°): | 52 | [23 empty] | tilt angle (°): | 53 | [23 empty] | tilt angle (°): | 54 | [23 empty] | tilt angle (°): | 55 | [23 empty] | tilt angle (°): | 56 | [23 empty] | tilt angle (°): | 57 | [23 empty] | tilt angle (°): | 58 | [23 empty] | tilt angle (°): | 59 | [23 empty] | tilt angle (°): | 60
| Monthly kWh/m2 | Tilt Angle (°) |  |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
| #N/A | #N/A |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sep | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jun | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jul | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sep | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jun | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jul | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sep | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jun | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jul | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sep | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jun | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jul | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sep | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Identified PV Space: | [25 empty] | Minimum Monthly HT bar: | #VALUE! | [25 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE!
[27 empty] | Corresponding tilt angle: | 10 | [25 empty] | 11 | [24 empty] | 12 | [24 empty] | 13 | [24 empty] | 14 | [24 empty] | 15 | [24 empty] | 16 | [24 empty] | 17 | [24 empty] | 18 | [24 empty] | 19 | [24 empty] | 20 | [24 empty] | 21 | [24 empty] | 22 | [24 empty] | 23 | [24 empty] | 24 | [24 empty] | 25 | [24 empty] | 26 | [24 empty] | 27 | [24 empty] | 28 | [24 empty] | 29 | [24 empty] | 30 | [24 empty] | 31 | [24 empty] | 32 | [24 empty] | 33 | [24 empty] | 34 | [24 empty] | 35 | [24 empty] | 36 | [24 empty] | 37 | [24 empty] | 38 | [24 empty] | 39 | [24 empty] | 40 | [24 empty] | 41 | [24 empty] | 42 | [24 empty] | 43 | [24 empty] | 44 | [24 empty] | 45 | [24 empty] | 46 | [24 empty] | 47 | [24 empty] | 48 | [24 empty] | 49 | [24 empty] | 50 | [24 empty] | 51 | [24 empty] | 52 | [24 empty] | 53 | [24 empty] | 54 | [24 empty] | 55 | [24 empty] | 56 | [24 empty] | 57 | [24 empty] | 58 | [24 empty] | 59 | [24 empty] | 60
[27 empty] | Max Minimum Monthly HT bar over tilt angles: | 0
[6 empty] | Exisiting roof tilt angle (°): | 0 | [19 empty] | Corresponding tilt angle to Max Minimum Monthly HT bar over tilt angles: | #N/A
| Output |  |  |  |  | surface azimuth angle (°): | 0 | [24 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0
[6 empty] | tilt angle (°): | 10 | [24 empty] | tilt angle (°): | 11 | [23 empty] | tilt angle (°): | 12 | [23 empty] | tilt angle (°): | 13 | [23 empty] | tilt angle (°): | 14 | [23 empty] | tilt angle (°): | 15 | [23 empty] | tilt angle (°): | 16 | [23 empty] | tilt angle (°): | 17 | [23 empty] | tilt angle (°): | 18 | [23 empty] | tilt angle (°): | 19 | [23 empty] | tilt angle (°): | 20 | [23 empty] | tilt angle (°): | 21 | [23 empty] | tilt angle (°): | 22 | [23 empty] | tilt angle (°): | 23 | [23 empty] | tilt angle (°): | 24 | [23 empty] | tilt angle (°): | 25 | [23 empty] | tilt angle (°): | 26 | [23 empty] | tilt angle (°): | 27 | [23 empty] | tilt angle (°): | 28 | [23 empty] | tilt angle (°): | 29 | [23 empty] | tilt angle (°): | 30 | [23 empty] | tilt angle (°): | 31 | [23 empty] | tilt angle (°): | 32 | [23 empty] | tilt angle (°): | 33 | [23 empty] | tilt angle (°): | 34 | [23 empty] | tilt angle (°): | 35 | [23 empty] | tilt angle (°): | 36 | [23 empty] | tilt angle (°): | 37 | [23 empty] | tilt angle (°): | 38 | [23 empty] | tilt angle (°): | 39 | [23 empty] | tilt angle (°): | 40 | [23 empty] | tilt angle (°): | 41 | [23 empty] | tilt angle (°): | 42 | [23 empty] | tilt angle (°): | 43 | [23 empty] | tilt angle (°): | 44 | [23 empty] | tilt angle (°): | 45 | [23 empty] | tilt angle (°): | 46 | [23 empty] | tilt angle (°): | 47 | [23 empty] | tilt angle (°): | 48 | [23 empty] | tilt angle (°): | 49 | [23 empty] | tilt angle (°): | 50 | [23 empty] | tilt angle (°): | 51 | [23 empty] | tilt angle (°): | 52 | [23 empty] | tilt angle (°): | 53 | [23 empty] | tilt angle (°): | 54 | [23 empty] | tilt angle (°): | 55 | [23 empty] | tilt angle (°): | 56 | [23 empty] | tilt angle (°): | 57 | [23 empty] | tilt angle (°): | 58 | [23 empty] | tilt angle (°): | 59 | [23 empty] | tilt angle (°): | 60
| Monthly kWh/m2 | Tilt Angle (°) |  |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
| #N/A | #N/A |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sep | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jun | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jul | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sep | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jun | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jul | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sep | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jun | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jul | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sep | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jun | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jul | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sep | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Identified PV Space: Ideal Pole Mount | [25 empty] | Minimum Monthly HT bar: | #VALUE! | [25 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE! | [24 empty] | #VALUE!
[27 empty] | Corresponding tilt angle: | 10 | [25 empty] | 11 | [24 empty] | 12 | [24 empty] | 13 | [24 empty] | 14 | [24 empty] | 15 | [24 empty] | 16 | [24 empty] | 17 | [24 empty] | 18 | [24 empty] | 19 | [24 empty] | 20 | [24 empty] | 21 | [24 empty] | 22 | [24 empty] | 23 | [24 empty] | 24 | [24 empty] | 25 | [24 empty] | 26 | [24 empty] | 27 | [24 empty] | 28 | [24 empty] | 29 | [24 empty] | 30 | [24 empty] | 31 | [24 empty] | 32 | [24 empty] | 33 | [24 empty] | 34 | [24 empty] | 35 | [24 empty] | 36 | [24 empty] | 37 | [24 empty] | 38 | [24 empty] | 39 | [24 empty] | 40 | [24 empty] | 41 | [24 empty] | 42 | [24 empty] | 43 | [24 empty] | 44 | [24 empty] | 45 | [24 empty] | 46 | [24 empty] | 47 | [24 empty] | 48 | [24 empty] | 49 | [24 empty] | 50 | [24 empty] | 51 | [24 empty] | 52 | [24 empty] | 53 | [24 empty] | 54 | [24 empty] | 55 | [24 empty] | 56 | [24 empty] | 57 | [24 empty] | 58 | [24 empty] | 59 | [24 empty] | 60
[27 empty] | Max Minimum Monthly HT bar over tilt angles: | 0
[27 empty] | Corresponding tilt angle to Max Minimum Monthly HT bar over tilt angles: | #N/A
| Output |  |  |  |  | surface azimuth angle (°): | 0 | [24 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0 | [23 empty] | surface azimuth angle (°): | 0
[6 empty] | tilt angle (°): | 10 | [24 empty] | tilt angle (°): | 11 | [23 empty] | tilt angle (°): | 12 | [23 empty] | tilt angle (°): | 13 | [23 empty] | tilt angle (°): | 14 | [23 empty] | tilt angle (°): | 15 | [23 empty] | tilt angle (°): | 16 | [23 empty] | tilt angle (°): | 17 | [23 empty] | tilt angle (°): | 18 | [23 empty] | tilt angle (°): | 19 | [23 empty] | tilt angle (°): | 20 | [23 empty] | tilt angle (°): | 21 | [23 empty] | tilt angle (°): | 22 | [23 empty] | tilt angle (°): | 23 | [23 empty] | tilt angle (°): | 24 | [23 empty] | tilt angle (°): | 25 | [23 empty] | tilt angle (°): | 26 | [23 empty] | tilt angle (°): | 27 | [23 empty] | tilt angle (°): | 28 | [23 empty] | tilt angle (°): | 29 | [23 empty] | tilt angle (°): | 30 | [23 empty] | tilt angle (°): | 31 | [23 empty] | tilt angle (°): | 32 | [23 empty] | tilt angle (°): | 33 | [23 empty] | tilt angle (°): | 34 | [23 empty] | tilt angle (°): | 35 | [23 empty] | tilt angle (°): | 36 | [23 empty] | tilt angle (°): | 37 | [23 empty] | tilt angle (°): | 38 | [23 empty] | tilt angle (°): | 39 | [23 empty] | tilt angle (°): | 40 | [23 empty] | tilt angle (°): | 41 | [23 empty] | tilt angle (°): | 42 | [23 empty] | tilt angle (°): | 43 | [23 empty] | tilt angle (°): | 44 | [23 empty] | tilt angle (°): | 45 | [23 empty] | tilt angle (°): | 46 | [23 empty] | tilt angle (°): | 47 | [23 empty] | tilt angle (°): | 48 | [23 empty] | tilt angle (°): | 49 | [23 empty] | tilt angle (°): | 50 | [23 empty] | tilt angle (°): | 51 | [23 empty] | tilt angle (°): | 52 | [23 empty] | tilt angle (°): | 53 | [23 empty] | tilt angle (°): | 54 | [23 empty] | tilt angle (°): | 55 | [23 empty] | tilt angle (°): | 56 | [23 empty] | tilt angle (°): | 57 | [23 empty] | tilt angle (°): | 58 | [23 empty] | tilt angle (°): | 59 | [23 empty] | tilt angle (°): | 60
| Monthly kWh/m2 | Tilt Angle (°) |  |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2) |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
| #N/A | #N/A |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sep | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jun | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jul | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sep | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jun | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jul | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sep | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jun | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jul | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sep | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Feb | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Mar | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Apr | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | May | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jun | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jul | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sep | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Jan | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| #N/A |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
The dark pink tables below are for determining the surface azimuth angle for a pole-mounted array at a specified tilt
These are not currently used in the spreadsheet, but could be programmed to be used if needed.
[9 empty] | tilt angle β (°): | #N/A
| Output | [8 empty] | surface azimuth angle (°): | A: -180
| Monthly kWh/m2 | Surface Azimuth Angle associated with the Max Min Monthly HT bar (°) | Min Monthly HT bar (MJ/m2) | Surface Azimuth Angle | Surface Azimuth Angle with concat month | Max Min Monthly HT bar (MJ/m2) |  |  | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
#N/A | #N/A | #N/A | #N/A | -180 | -180,Jan | #N/A |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
#N/A | #N/A |  |  |  | -180,Feb |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
#N/A | #N/A |  |  |  | -180,Mar |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
#N/A | #N/A |  |  |  | -180,Apr |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
#N/A | #N/A |  |  |  | -180,May |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
#N/A | #N/A |  |  |  | -180,June |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
#N/A | #N/A |  |  |  | -180,July |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
#N/A | #N/A |  |  |  | -180,Aug |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
#N/A | #N/A |  |  |  | -180,Sept |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
#N/A | #N/A |  |  |  | -180,Oct |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
#N/A | #N/A |  |  |  | -180,Nov |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
#N/A | #N/A |  |  |  | -180,Dec |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[10 empty] | surface azimuth angle (°): | -170
[9 empty] | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
|  |  | #N/A | -170 | -170,Jan |  |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -170,Feb |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -170,Mar |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -170,Apr |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -170,May |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -170,June |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -170,July |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -170,Aug |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -170,Sept |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -170,Oct |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -170,Nov |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -170,Dec |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[10 empty] | surface azimuth angle (°): | -160
[9 empty] | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
|  |  | #N/A | -160 | -160,Jan |  |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -160,Feb |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -160,Mar |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -160,Apr |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -160,May |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -160,June |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -160,July |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -160,Aug |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -160,Sept |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -160,Oct |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -160,Nov |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -160,Dec |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[10 empty] | surface azimuth angle (°): | -150
[9 empty] | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
|  |  | #N/A | -150 | -150,Jan |  |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -150,Feb |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -150,Mar |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -150,Apr |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -150,May |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -150,June |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -150,July |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -150,Aug |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -150,Sept |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -150,Oct |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -150,Nov |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -150,Dec |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[10 empty] | surface azimuth angle (°): | -140
[9 empty] | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
|  |  | #N/A | -140 | -140,Jan |  |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -140,Feb |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -140,Mar |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -140,Apr |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -140,May |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -140,June |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -140,July |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -140,Aug |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -140,Sept |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -140,Oct |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -140,Nov |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -140,Dec |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[10 empty] | surface azimuth angle (°): | -130
[9 empty] | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
|  |  | #N/A | -130 | -130,Jan |  |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -130,Feb |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -130,Mar |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -130,Apr |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -130,May |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -130,June |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -130,July |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -130,Aug |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -130,Sept |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -130,Oct |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -130,Nov |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -130,Dec |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[10 empty] | surface azimuth angle (°): | -120
[9 empty] | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
|  |  | #N/A | -120 | -120,Jan |  |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -120,Feb |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -120,Mar |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -120,Apr |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -120,May |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -120,June |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -120,July |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -120,Aug |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -120,Sept |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -120,Oct |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -120,Nov |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -120,Dec |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[10 empty] | surface azimuth angle (°): | -110
[9 empty] | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
|  |  | #N/A | -110 | -110,Jan |  |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -110,Feb |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -110,Mar |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -110,Apr |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -110,May |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -110,June |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -110,July |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -110,Aug |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -110,Sept |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -110,Oct |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -110,Nov |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -110,Dec |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[10 empty] | surface azimuth angle (°): | -100
[9 empty] | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
|  |  | #N/A | -100 | -100,Jan |  |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -100,Feb |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -100,Mar |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -100,Apr |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -100,May |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -100,June |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -100,July |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -100,Aug |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -100,Sept |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -100,Oct |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -100,Nov |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -100,Dec |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[10 empty] | surface azimuth angle (°): | -90
[9 empty] | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
|  |  | #N/A | -90 | -90,Jan |  |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -90,Feb |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -90,Mar |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -90,Apr |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -90,May |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -90,June |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -90,July |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -90,Aug |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -90,Sept |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -90,Oct |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -90,Nov |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -90,Dec |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[10 empty] | surface azimuth angle (°): | -80
[9 empty] | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
|  |  | #N/A | -80 | -80,Jan |  |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -80,Feb |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -80,Mar |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -80,Apr |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -80,May |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -80,June |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -80,July |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -80,Aug |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -80,Sept |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -80,Oct |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -80,Nov |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -80,Dec |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[10 empty] | surface azimuth angle (°): | -70
[9 empty] | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
|  |  | #N/A | -70 | -70,Jan |  |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -70,Feb |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -70,Mar |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -70,Apr |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -70,May |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -70,June |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -70,July |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -70,Aug |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -70,Sept |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -70,Oct |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -70,Nov |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -70,Dec |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[10 empty] | surface azimuth angle (°): | -60
[9 empty] | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
|  |  | #N/A | -60 | -60,Jan |  |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -60,Feb |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -60,Mar |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -60,Apr |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -60,May |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -60,June |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -60,July |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -60,Aug |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -60,Sept |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -60,Oct |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -60,Nov |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -60,Dec |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[10 empty] | surface azimuth angle (°): | -50
[9 empty] | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
|  |  | #N/A | -50 | -50,Jan |  |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -50,Feb |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -50,Mar |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -50,Apr |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -50,May |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -50,June |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -50,July |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -50,Aug |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -50,Sept |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -50,Oct |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -50,Nov |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -50,Dec |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[10 empty] | surface azimuth angle (°): | -40
[9 empty] | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
|  |  | #N/A | -40 | -40,Jan |  |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -40,Feb |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -40,Mar |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -40,Apr |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -40,May |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -40,June |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -40,July |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -40,Aug |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -40,Sept |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -40,Oct |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -40,Nov |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -40,Dec |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[10 empty] | surface azimuth angle (°): | -30
[9 empty] | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
|  |  | #N/A | -30 | -30,Jan |  |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -30,Feb |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -30,Mar |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -30,Apr |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -30,May |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -30,June |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -30,July |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -30,Aug |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -30,Sept |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -30,Oct |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -30,Nov |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -30,Dec |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[10 empty] | surface azimuth angle (°): | -20
[9 empty] | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
|  |  | #N/A | -20 | -20,Jan |  |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -20,Feb |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -20,Mar |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -20,Apr |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -20,May |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -20,June |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -20,July |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -20,Aug |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -20,Sept |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -20,Oct |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -20,Nov |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -20,Dec |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[10 empty] | surface azimuth angle (°): | -10
[9 empty] | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
|  |  | #N/A | -10 | -10,Jan |  |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -10,Feb |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -10,Mar |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -10,Apr |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -10,May |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -10,June |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -10,July |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -10,Aug |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -10,Sept |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -10,Oct |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -10,Nov |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | -10,Dec |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[10 empty] | surface azimuth angle (°): | 0
[9 empty] | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
|  |  | #N/A | 0 | 0,Jan |  |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 0,Feb |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 0,Mar |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 0,Apr |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 0,May |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 0,June |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 0,July |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 0,Aug |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 0,Sept |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 0,Oct |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 0,Nov |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 0,Dec |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[10 empty] | surface azimuth angle (°): | 10
[9 empty] | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
|  |  | #N/A | 10 | 10,Jan |  |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 10,Feb |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 10,Mar |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 10,Apr |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 10,May |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 10,June |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 10,July |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 10,Aug |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 10,Sept |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 10,Oct |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 10,Nov |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 10,Dec |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[10 empty] | surface azimuth angle (°): | 20
[9 empty] | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
|  |  | #N/A | 20 | 20,Jan |  |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 20,Feb |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 20,Mar |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 20,Apr |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 20,May |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 20,June |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 20,July |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 20,Aug |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 20,Sept |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 20,Oct |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 20,Nov |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 20,Dec |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[10 empty] | surface azimuth angle (°): | 30
[9 empty] | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
|  |  | #N/A | 30 | 30,Jan |  |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 30,Feb |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 30,Mar |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 30,Apr |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 30,May |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 30,June |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 30,July |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 30,Aug |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 30,Sept |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 30,Oct |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 30,Nov |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 30,Dec |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[10 empty] | surface azimuth angle (°): | 40
[9 empty] | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
|  |  | #N/A | 40 | 40,Jan |  |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 40,Feb |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 40,Mar |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 40,Apr |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 40,May |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 40,June |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 40,July |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 40,Aug |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 40,Sept |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 40,Oct |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 40,Nov |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 40,Dec |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[10 empty] | surface azimuth angle (°): | 50
[9 empty] | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
|  |  | #N/A | 50 | 50,Jan |  |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 50,Feb |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 50,Mar |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 50,Apr |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 50,May |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 50,June |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 50,July |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 50,Aug |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 50,Sept |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 50,Oct |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 50,Nov |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 50,Dec |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[10 empty] | surface azimuth angle (°): | 60
[9 empty] | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
|  |  | #N/A | 60 | 60,Jan |  |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 60,Feb |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 60,Mar |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 60,Apr |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 60,May |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 60,June |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 60,July |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 60,Aug |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 60,Sept |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 60,Oct |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 60,Nov |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 60,Dec |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[10 empty] | surface azimuth angle (°): | 70
[9 empty] | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
|  |  | #N/A | 70 | 70,Jan |  |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 70,Feb |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 70,Mar |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 70,Apr |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 70,May |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 70,June |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 70,July |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 70,Aug |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 70,Sept |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 70,Oct |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 70,Nov |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 70,Dec |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[10 empty] | surface azimuth angle (°): | 80
[9 empty] | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
|  |  | #N/A | 80 | 80,Jan |  |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 80,Feb |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 80,Mar |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 80,Apr |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 80,May |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 80,June |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 80,July |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 80,Aug |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 80,Sept |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 80,Oct |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 80,Nov |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 80,Dec |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[10 empty] | surface azimuth angle (°): | 90
[9 empty] | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
|  |  | #N/A | 90 | 90,Jan |  |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 90,Feb |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 90,Mar |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 90,Apr |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 90,May |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 90,June |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 90,July |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 90,Aug |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 90,Sept |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 90,Oct |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 90,Nov |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 90,Dec |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[10 empty] | surface azimuth angle (°): | 100
[9 empty] | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
|  |  | #N/A | 100 | 100,Jan |  |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 100,Feb |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 100,Mar |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 100,Apr |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 100,May |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 100,June |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 100,July |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 100,Aug |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 100,Sept |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 100,Oct |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 100,Nov |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 100,Dec |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[10 empty] | surface azimuth angle (°): | 110
[9 empty] | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
|  |  | #N/A | 110 | 110,Jan |  |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 110,Feb |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 110,Mar |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 110,Apr |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 110,May |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 110,June |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 110,July |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 110,Aug |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 110,Sept |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 110,Oct |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 110,Nov |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 110,Dec |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[10 empty] | surface azimuth angle (°): | 120
[9 empty] | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
|  |  | #N/A | 120 | 120,Jan |  |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 120,Feb |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 120,Mar |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 120,Apr |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 120,May |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 120,June |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 120,July |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 120,Aug |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 120,Sept |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 120,Oct |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 120,Nov |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 120,Dec |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[10 empty] | surface azimuth angle (°): | 130
[9 empty] | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
|  |  | #N/A | 130 | 130,Jan |  |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 130,Feb |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 130,Mar |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 130,Apr |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 130,May |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 130,June |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 130,July |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 130,Aug |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 130,Sept |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 130,Oct |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 130,Nov |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 130,Dec |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[10 empty] | surface azimuth angle (°): | 140
[9 empty] | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
|  |  | #N/A | 140 | 140,Jan |  |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 140,Feb |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 140,Mar |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 140,Apr |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 140,May |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 140,June |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 140,July |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 140,Aug |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 140,Sept |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 140,Oct |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 140,Nov |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 140,Dec |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[10 empty] | surface azimuth angle (°): | 150
[9 empty] | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
|  |  | #N/A | 150 | 150,Jan |  |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 150,Feb |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 150,Mar |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 150,Apr |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 150,May |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 150,June |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 150,July |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 150,Aug |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 150,Sept |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 150,Oct |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 150,Nov |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 150,Dec |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[10 empty] | surface azimuth angle (°): | 160
[9 empty] | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
|  |  | #N/A | 160 | 160,Jan |  |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 160,Feb |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 160,Mar |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 160,Apr |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 160,May |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 160,June |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 160,July |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 160,Aug |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 160,Sept |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 160,Oct |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 160,Nov |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 160,Dec |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[10 empty] | surface azimuth angle (°): | 170
[9 empty] | n | declination (б) | ωs | rightful Hd/H bar | Inputed Ave Monthly reflectance factor (ρg) | Inputed Ave Monthly Insolation (Ĥ) (J/m2/day) | A | B | C | ¦ωss¦ | ωss | ¦ωsr¦ | ωsr | a | b | d | a' | G(ωss,ωsr) | G(ωss,-ωs) | G(ωs,ωsr) | D | Rbar | Daily HT bar (MJ/m2) | Monthly HT bar (MJ/m2)
|  |  | #N/A | 170 | 170,Jan |  |  | Jan | 17 | -20.917 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 170,Feb |  |  | Feb | 47 | -12.9546 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 170,Mar |  |  | Mar | 75 | -2.4177 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 170,Apr |  |  | Apr | 105 | 9.4149 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 170,May |  |  | May | 135 | 18.7919 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 170,June |  |  | June | 162 | 23.0859 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 170,July |  |  | July | 198 | 21.1837 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 170,Aug |  |  | Aug | 228 | 13.455 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 170,Sept |  |  | Sept | 258 | 2.2169 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 170,Oct |  |  | Oct | 288 | -9.5994 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 170,Nov |  |  | Nov | 318 | -18.912 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
[5 empty] | 170,Dec |  |  | Dec | 344 | -23.0496 | #VALUE! | #VALUE! | 0 | 0 | #N/A | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #N/A | #N/A | #N/A | #N/A
Note on AC39: Meg: This calculates the maximum of the minimum monthly insolation while ignoring errors. Function is AGGREGATE(), where the number 4 specifies MAX, the number 6 specifies the option to ignore errors.
Note on AC60: Meg: This calculates the maximum of the minimum monthly insolation while ignoring errors. Function is AGGREGATE(), where the number 4 specifies MAX, the number 6 specifies the option to ignore errors.
Note on AC81: Meg: This calculates the maximum of the minimum monthly insolation while ignoring errors. Function is AGGREGATE(), where the number 4 specifies MAX, the number 6 specifies the option to ignore errors.
Note on AC102: Meg: This calculates the maximum of the minimum monthly insolation while ignoring errors. Function is AGGREGATE(), where the number 4 specifies MAX, the number 6 specifies the option to ignore errors.